## ACS Requirements
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text
001 | Access Control Specification | Cyber Security | ACS-001 | All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches.
002 | Access Control Specification | Cyber Security | ACS-002 | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks.
003 | Access Control Specification |  | ACS-003 | Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply.
004 | Access Control Specification |  | ACS-004 | ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS.
005 | Access Control Specification |  | ACS-005 | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits.
006 | Access Control Specification |  | ACS-006 | Opening of a protected ACS enclosure shall generate an alarm at the central security workstation.
007 | Access Control Specification |  | ACS-007 | Duress buttons shall be installed at control room entrances and security desks.
008 | Access Control Specification |  | ACS-008 | Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP).
009 | Access Control Specification |  | ACS-009 | Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling.
010 | Access Control Specification |  | ACS-010 | ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements.
011 | Access Control Specification |  | ACS-011 | Each access-controlled door shall include a door position switch for monitoring door open and closed status.
012 | Access Control Specification |  | ACS-012 | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller.
013 | Access Control Specification |  | ACS-013 | Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification.
014 | Access Control Specification |  | ACS-014 | Card readers installed in hazardous areas shall be certified for the applicable area classification.
015 | Access Control Specification | Cyber Security | ACS-015 | ACS controllers shall retain local decision-making capability during network communication loss.
016 | Access Control Specification | Cyber Security | ACS-016 | ACS event logs shall be buffered locally for a minimum of 10000 events during network outage.
017 | Access Control Specification |  | ACS-017 | All ACS field wiring shall be clearly labeled at both ends using permanent machine-printed labels.
018 | Access Control Specification |  | ACS-018 | ACS control panels shall include surge protection for power and communication interfaces.
019 | Access Control Specification |  | ACS-019 | Door lock power circuits shall be individually fused or electronically protected against overcurrent.
020 | Access Control Specification | Cyber Security | ACS-020 | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources.
097 | Access Control Specification | Cyber Security | ACS-021 | The ACS shall support anti-passback logic to prevent credential sharing and unauthorized re-entry.
098 | Access Control Specification | Cyber Security | ACS-022 | The ACS credential database shall be automatically backed up daily to a secure redundant storage location.
099 | Access Control Specification | Safety | ACS-023 | The ACS shall generate a forced-open alarm when a controlled door remains open longer than the configured timeout period.
100 | Access Control Specification | Cyber Security | ACS-024 | Central ACS servers shall be deployed in a redundant primary-secondary architecture with automatic failover.
101 | Access Control Specification |  | ACS-025 | The ACS shall support integration with the video management system for alarm-triggered video association.