## Company Standard
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text
049 | Electrical Design Basis Specification |  | EDB-049 | Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution.
050 | Electrical Design Basis Specification |  | EDB-050 | Steady-state voltage drop at utilization equipment shall not exceed 5%.
051 | Electrical Design Basis Specification | Safety | EDB-051 | System voltage drop during automatic reacceleration of motors shall not exceed 15%.
052 | Electrical Design Basis Specification | Safety | EDB-052 | Electrical equipment short-circuit ratings shall exceed the maximum available fault current.
053 | Electrical Design Basis Specification | Safety | EDB-053 | Equipment installed in classified locations shall comply with NFPA 70 requirements.
054 | Electrical Design Basis Specification | Safety | EDB-054 | Explosion-proof equipment shall be used in Class I Division 1 locations.
055 | Electrical Design Basis Specification | Safety | EDB-055 | All electrical equipment shall be grounded and bonded to the plant grounding grid.
056 | Electrical Design Basis Specification | Safety | EDB-056 | Arc flash warning labels shall be installed on energized equipment.
057 | Electrical Design Basis Specification |  | EDB-057 | Power transformers shall be oil-filled ONAN type.
058 | Electrical Design Basis Specification |  | EDB-058 | Transformer impedance shall be 5.75% nominal.
059 | Electrical Design Basis Specification |  | EDB-059 | Transformers shall have 65°C temperature rise with Class OA insulation.
060 | Electrical Design Basis Specification |  | EDB-060 | Motor starters shall be across-the-line type unless otherwise specified.
061 | Electrical Design Basis Specification | Safety | EDB-061 | Each motor starter shall include a local disconnecting device.
062 | Electrical Design Basis Specification | Safety | EDB-062 | Motor starters shall include overload, short-circuit, and phase-loss protection.
063 | Electrical Design Basis Specification | Safety | EDB-063 | Automatic motor reacceleration shall occur in priority sequence after voltage restoration.
064 | Electrical Design Basis Specification | Safety | EDB-064 | Standby generators shall be provided for critical loads.
065 | Electrical Design Basis Specification |  | EDB-065 | Standby generators shall be diesel engine driven.
066 | Electrical Design Basis Specification | Safety | EDB-066 | Automatic transfer switches shall be provided for emergency loads.
067 | Electrical Design Basis Specification |  | EDB-067 | Transfer to standby power shall occur within 30 seconds.
068 | Electrical Design Basis Specification |  | EDB-068 | Wire and cable terminations at motors shall use compression lugs.
069 | Electrical Design Basis Specification | Safety | EDB-069 | Cable glands in classified areas shall be explosion-proof rated.
070 | Electrical Design Basis Specification |  | EDB-070 | Cable ampacity shall be derated for ambient temperature and grouping.
071 | Electrical Design Basis Specification |  | EDB-071 | Power and instrumentation cables shall be installed in separate tray systems.
072 | Electrical Design Basis Specification | Safety | EDB-072 | Circuit breakers shall have minimum interrupting rating of 35 kA.
073 | Electrical Design Basis Specification | Safety | EDB-073 | Protective device coordination studies shall be performed.
074 | Electrical Design Basis Specification | Cyber Security | EDB-074 | Protective relays shall communicate alarms to the substation HMI.
075 | Electrical Design Basis Specification | Safety | EDB-075 | Substation alarms shall include transformer trip, breaker trip, and ground fault.
076 | Electrical Design Basis Specification | Cyber Security | EDB-076 | Electrical monitoring systems shall integrate with plant SCADA.