## Facility Security Systems
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text
077 | Facility Security Systems Specification | Cyber Security | FSS-101 | Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources.
078 | Facility Security Systems Specification |  | FSS-102 | Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches.
079 | Facility Security Systems Specification | Cyber Security | FSS-103 | Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks.
080 | Facility Security Systems Specification |  | FSS-104 | Security control panels shall include surge protection on power, communications, and field I/O circuits.
081 | Facility Security Systems Specification | Safety | FSS-105 | Card readers and field security devices installed in hazardous classified areas shall be certified for the applicable area classification.
082 | Facility Security Systems Specification |  | FSS-106 | Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs.
083 | Facility Security Systems Specification |  | FSS-107 | Access-controlled doors shall include door position monitoring to indicate secure, open, and forced-open conditions.
084 | Facility Security Systems Specification |  | FSS-108 | Access-controlled doors shall include request-to-exit devices connected to the door controller.
085 | Facility Security Systems Specification |  | FSS-109 | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits.
086 | Facility Security Systems Specification |  | FSS-110 | Opening of a protected security enclosure shall generate an alarm at the central security workstation.
087 | Facility Security Systems Specification | Safety | FSS-111 | Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations.
088 | Facility Security Systems Specification |  | FSS-112 | Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling.
089 | Facility Security Systems Specification |  | FSS-113 | Facility security system cabling shall be shielded twisted pair or fiber optic cable suitable for the installed environment.
090 | Facility Security Systems Specification |  | FSS-114 | Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard.
091 | Facility Security Systems Specification | Cyber Security | FSS-115 | Security system event logs shall be retained locally during network outages and forwarded to the security workstation when communications are restored.
092 | Facility Security Systems Specification |  | FSS-116 | Security controllers shall support local access decisions during loss of communication with the central server.
093 | Facility Security Systems Specification | Safety | FSS-117 | Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis.
094 | Facility Security Systems Specification |  | FSS-118 | Security field wiring shall be permanently labeled at both ends, and spare conductors shall be identified and isolated.
095 | Facility Security Systems Specification |  | FSS-119 | Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions.
096 | Facility Security Systems Specification | Cyber Security | FSS-120 | The security system shall record access control events, door alarms, enclosure tamper events, and operator actions in an auditable event log.