## Company Standard
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text
021 | Liquid Custody Transfer Specification |  | FM-021 | The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions.
022 | Liquid Custody Transfer Specification |  | FM-022 | Verification meters shall be provided to confirm primary meter performance.
023 | Liquid Custody Transfer Specification |  | FM-023 | The metering system shall operate over a flow range of 20% to 100% of design flow.
024 | Liquid Custody Transfer Specification |  | FM-024 | Overall measurement uncertainty shall not exceed ±0.25% of indicated volume.
025 | Liquid Custody Transfer Specification |  | FM-025 | All custody transfer meters, provers, and flow computers shall include locks or tamper seals.
026 | Liquid Custody Transfer Specification | Cyber Security | FM-026 | Electronic access to flow computers shall require authenticated user credentials.
027 | Liquid Custody Transfer Specification | Cyber Security | FM-027 | All metering parameter changes shall be recorded in an audit log.
028 | Liquid Custody Transfer Specification | Cyber Security | FM-028 | Calibration settings shall be password protected.
029 | Liquid Custody Transfer Specification | Safety | FM-029 | All electrical equipment installed in hazardous areas shall comply with IEC 60079.
030 | Liquid Custody Transfer Specification | Safety | FM-030 | Intrinsic safety barriers shall be provided for field instrumentation in classified areas.
031 | Liquid Custody Transfer Specification | Safety | FM-031 | All meter station equipment shall be properly grounded and bonded.
032 | Liquid Custody Transfer Specification |  | FM-032 | Meter stations shall allow safe access for operation and maintenance.
033 | Liquid Custody Transfer Specification |  | FM-033 | A minimum upstream straight pipe length of 10 diameters shall be provided.
034 | Liquid Custody Transfer Specification |  | FM-034 | A minimum downstream straight pipe length of 5 diameters shall be provided.
035 | Liquid Custody Transfer Specification |  | FM-035 | Meter headers shall be designed to minimize flow disturbances.
036 | Liquid Custody Transfer Specification | Safety | FM-036 | Isolation valves shall be installed upstream and downstream of each meter.
037 | Liquid Custody Transfer Specification | Safety | FM-037 | Double block and bleed isolation shall be provided for prover connections.
038 | Liquid Custody Transfer Specification |  | FM-038 | Meter bypass lines shall remain sealed closed during normal operation.
039 | Liquid Custody Transfer Specification | Environmental | FM-039 | Drain connections shall discharge to a closed drain system.
040 | Liquid Custody Transfer Specification | Environmental | FM-040 | Fill connections shall permit safe priming of meter runs.
041 | Liquid Custody Transfer Specification | Environmental | FM-041 | Blowdown connections shall route fluids to a closed recovery system.
042 | Liquid Custody Transfer Specification |  | FM-042 | Pressure transmitters shall have an accuracy of ±0.1% of span.
043 | Liquid Custody Transfer Specification |  | FM-043 | Temperature sensing elements shall be RTDs with accuracy of ±0.2°C.
044 | Liquid Custody Transfer Specification | Cyber Security | FM-044 | A dedicated flow computer shall perform custody transfer calculations.
045 | Liquid Custody Transfer Specification |  | FM-045 | Critical measurement signals shall use redundant signal paths.
046 | Liquid Custody Transfer Specification |  | FM-046 | Metering data shall be archived in the facility historian.
047 | Liquid Custody Transfer Specification |  | FM-047 | Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8.
048 | Liquid Custody Transfer Specification |  | FM-048 | Custody transfer meters shall be verified every 6 months.