## Project Spec
Requirement ID | Special Code | Requirement Text
7.1.1 |  | Each access-controlled door shall include redundant door position switches for monitoring secure and open status.
7.1.2 |  | The access control panel power system shall include the following: each ACS control panel shall be powered from a dedicated 48 VDC regulated power supply; power supplies shall be mounted in lockable enclosures; and each power supply output shall be protected against overcurrent.
7.1.3 |  | ACS control panels shall include surge protection for all power, communication, and I/O interfaces.
7.1.4 |  | All ACS field panels, intelligent door controllers, IP-based card readers, and biometric readers shall connect to the PROJECT security network using managed Layer 3 Ethernet switches.
7.2.1 | Safety | Card readers installed in hazardous areas shall be certified for Zone 1 hazardous area classification per IEC 60079.
7.2.2 | Cyber Security | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources.
7.2.3 |  | The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms.
7.2.4 |  | Inter-building ACS communication links exceeding 90 m shall use multimode fiber optic cabling.
7.3.1 | Cyber Security | ACS event logs shall be buffered locally for a minimum of 20000 events during network outage.
7.3.2 |  | ACS equipment shall maintain full operational capability for 8 hours following loss of primary power using UPS and battery backup.
7.3.3 |  | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller.
7.3.4 | Cyber Security | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks.
7.4.1 | Safety | Duress buttons shall be installed at control room entrances, security desks, and gatehouses.
7.4.2 |  | ACS controllers shall retain autonomous local decision-making capability during network communication loss for a minimum of 24 hours.
7.4.3 |  | ACS equipment grounding shall comply with BICSI TDMM telecommunications grounding and bonding requirements.
7.4.4 |  | All ACS control enclosures, reader junction boxes, field panels, and power supply cabinets shall include supervised tamper circuits.
7.5.1 |  | Door lock power circuits shall be individually fused and continuously monitored for overcurrent conditions.
7.5.2 |  | Copper ACS communication cabling shall be Category 6A shielded twisted pair (STP).
7.5.3 | Safety | Electric locking hardware shall fail safe or fail secure as defined in the PROJECT Facility Design Specification and fire alarm cause-and-effect matrix.
7.5.4 |  | ACS field installation requirements shall include the following: all ACS field wiring shall be labeled at both ends using permanent engraved labels; cable shields shall be terminated in accordance with the grounding standard; and spare conductors shall be identified and isolated.