## Project Spec
Requirement ID | Special Code | Requirement Text
8.1.1 |  | Power transformers shall be dry-type cast resin transformers.
8.1.2 |  | PROJECT nominal system voltages shall be 480 V, 6.6 kV, and 13.8 kV for low and medium voltage distribution.
8.1.3 | Safety | Circuit breakers shall have minimum interrupting rating of 50 kA.
8.1.4 | Safety | Equipment installed in classified locations shall comply with IEC 60364 requirements.
8.2.1 |  | Transfer to standby power shall occur within 10 seconds.
8.2.2 |  | Motor starters shall be VFD type for motors above 100 hp unless otherwise specified.
8.2.3 |  | Steady-state voltage drop at utilization equipment shall not exceed 3%.
8.2.4 | Safety | Substation alarms shall include transformer trip, breaker trip, ground fault, and fire alarm.
8.3.1 | Safety | Standby generators shall be provided for all critical process and safety loads.
8.3.2 | Safety | All PROJECT electrical equipment shall be grounded, bonded, and surge protected.
8.3.3 |  | Power and instrumentation cables shall be installed in separate tray systems with 300 mm separation.
8.4.1 |  | Transformer impedance shall be 6.5% nominal.
8.4.2 | Safety | Automatic motor reacceleration shall occur in configurable priority sequence after voltage restoration.
8.4.3 | Safety | The motor reacceleration study shall confirm that system voltage drop during automatic reacceleration of motors shall not exceed 10%. Motors shall be grouped by process priority, and each group shall be released only after bus voltage has recovered above the configured threshold.
8.4.4 | Cyber Security | Protective relays shall communicate alarms and events to the PROJECT substation HMI.
8.5.1 | Safety | Automatic transfer switches with bypass isolation shall be provided for emergency loads.
8.5.2 | Safety | Cable glands in classified areas shall be IEC certified explosion-proof rated.
8.5.3 | Safety | Explosion-proof equipment shall be used in Zone 1 classified locations.
8.5.4 | Cyber Security | Electrical monitoring systems shall integrate with PROJECT SCADA and historian.
8.6.1 | Safety | Each motor starter shall include a lockable local disconnecting device.
8.6.2 | Safety | Electrical equipment short-circuit ratings shall exceed the maximum calculated fault current by 10%.
8.6.3 |  | Standby generators shall be gas turbine driven.
8.6.4 |  | Transformers shall have 80°C temperature rise with Class F insulation.
8.7.1 | Safety | Protective device coordination and arc flash studies shall be performed.
8.7.2 |  | Wire and cable terminations at motors shall use compression lugs with heat shrink boots.
8.7.3 | Safety | Arc flash warning labels and incident energy values shall be installed on energized equipment.
8.7.4 |  | Cable ampacity shall be derated for ambient temperature, grouping, and solar loading.
8.7.5 | Safety | Motor starter protection shall include overload, short-circuit, phase-loss, and undervoltage protection. The protection settings shall be coordinated with upstream circuit breakers and documented in the protective device coordination study.