## Project Spec
Requirement ID | Special Code | Requirement Text
6.1.1 |  | A minimum upstream straight pipe length of 20 diameters shall be provided.
6.1.2 |  | The PROJECT crude receipt metering facility shall be designed for continuous custody transfer measurement during all operating scenarios.
6.1.3 |  | Flow meters shall be calibrated prior to commissioning per ISO 17089.
6.1.4 | Cyber Security | Electronic access to flow computers shall require multi-factor authenticated credentials.
6.2.1 | Environmental | Drain and liquid handling connections shall be designed as a closed system. Drain connections shall discharge to the oily water closed drain system, fill connections shall permit safe meter run priming and flushing, and blowdown connections shall route hydrocarbons to a vapor recovery system.
6.2.2 |  | Overall measurement uncertainty shall not exceed ±0.15% of indicated volume.
6.2.3 |  | Meter headers shall be designed to eliminate swirl and flow disturbances.
6.2.4 |  | Dual redundant pressure transmitters shall have an accuracy of ±0.05% of span.
6.3.1 | Safety | All electrical equipment installed in hazardous areas shall comply with NEMA 250 and project hazardous area classification requirements.
6.3.2 |  | Verification ultrasonic meters shall be provided to validate primary meter performance.
6.3.3 |  | Meter bypass lines shall remain locked and sealed closed during normal operation.
6.4.1 |  | Custody transfer meters shall be verified every 3 months.
6.4.2 | Cyber Security | All metering parameter changes shall be recorded in a secure audit log with timestamps.
6.4.3 | Safety | Full-port isolation valves shall be installed upstream and downstream of each meter.
6.4.4 |  | Temperature sensing elements shall be dual RTDs with accuracy of ±0.1°C.
6.5.1 |  | The metering system shall operate over a flow range of 10% to 100% of design flow.
6.5.2 | Environmental | Blowdown connections shall route hydrocarbons to a vapor recovery system.
6.5.3 | Safety | All meter station equipment shall be grounded, bonded, and surge protected.
6.5.4 |  | All custody transfer meters, provers, and flow computers shall include locks, tamper seals, or electronic access control.
6.6.1 | Cyber Security | A redundant flow computer pair shall perform custody transfer calculations. The flow computer configuration shall support role-based access, secure parameter downloads, and event transfer to the metering workstation.
6.6.2 |  | A minimum downstream straight pipe length of 10 diameters shall be provided.
6.6.3 | Environmental | Fill connections shall permit safe meter run priming and flushing.
6.6.4 | Cyber Security | Calibration settings shall be password protected and limited to administrator accounts.
6.7.1 |  | Metering data shall be archived in the PROJECT historian and backup server.
6.7.2 | Safety | Double block and bleed isolation shall be provided for prover and calibration connections.
6.7.3 | Safety | Redundant intrinsic safety barriers shall be provided for field instrumentation in classified areas.
6.7.4 |  | Critical measurement signals shall use dual redundant signal paths.
6.7.5 |  | The meter station layout shall support operation, maintenance, and proving activities. Meter stations shall allow safe operator access and maintenance clearance around meters, prover connections, isolation valves, drains, and instrument enclosures.