## Results
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text | Comparison Dataset - Requirement ID | Special Code | Comparison Dataset - Requirement Text | Score | Match Rank | Match Diagnostics
57 | Electrical Design Basis Specification | nan | EDB-057 | Power transformers shall be oil-filled ONAN type. | 8.1.1 | nan | Power transformers shall be dry-type cast resin transformers. | 0.459 | 1 | final=0.459; semantic=0.642; containment=0.000; fuzz=0.673; predicate_similarity=0.333; warnings=Borderline score; anchors=power,transformers,type; reference_object=power,transformers; comparison_object=power,transformers; reference_scope=none; comparison_scope=none
49 | Electrical Design Basis Specification | nan | EDB-049 | Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution. | 8.1.2 | nan | PROJECT nominal system voltages shall be 480 V, 6.6 kV, and 13.8 kV for low and medium voltage distribution. | 0.657 | 2 | final=0.657; semantic=0.933; containment=0.000; fuzz=0.946; predicate_similarity=1.000; warnings=None; anchors=distribution,medium,nominal,voltage,voltages; reference_object=nominal,voltages; comparison_object=nominal,project,voltages; reference_scope=low medium voltage distribution; comparison_scope=low medium voltage distribution
72 | Electrical Design Basis Specification | Safety | EDB-072 | Circuit breakers shall have minimum interrupting rating of 35 kA. | 8.1.3 | Safety | Circuit breakers shall have minimum interrupting rating of 50 kA. | 0.669 | 3 | final=0.669; semantic=0.934; containment=0.000; fuzz=0.985; predicate_similarity=1.000; warnings=None; anchors=breakers,circuit,have,interrupting,minimum,rating; reference_object=breakers,circuit; comparison_object=breakers,circuit; reference_scope=none; comparison_scope=none
53 | Electrical Design Basis Specification | Safety | EDB-053 | Equipment installed in classified locations shall comply with NFPA 70 requirements. | 8.1.4 | Safety | Equipment installed in classified locations shall comply with IEC 60364 requirements. | 0.537 | 4 | final=0.537; semantic=0.646; containment=0.000; fuzz=0.929; predicate_similarity=0.500; warnings=None; anchors=classified,comply,installed,locations; reference_object=classified,installed,locations; comparison_object=classified,installed,locations; reference_scope=none; comparison_scope=none
29 | Liquid Custody Transfer Specification | Safety | FM-029 | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | 8.1.4 | Safety | Equipment installed in classified locations shall comply with IEC 60364 requirements. | 0.484 | 5 | final=0.484; semantic=0.725; containment=0.000; fuzz=0.647; predicate_similarity=0.500; warnings=Borderline score ¦ Low anchor overlap; anchors=comply,installed; reference_object=areas,hazardous,installed; comparison_object=classified,installed,locations; reference_scope=none; comparison_scope=none
67 | Electrical Design Basis Specification | nan | EDB-067 | Transfer to standby power shall occur within 30 seconds. | 8.2.1 | nan | Transfer to standby power shall occur within 10 seconds. | 0.683 | 6 | final=0.683; semantic=0.971; containment=0.000; fuzz=0.982; predicate_similarity=1.000; warnings=None; anchors=occur,power,seconds,standby,transfer,within; reference_object=power,standby,transfer; comparison_object=power,standby,transfer; reference_scope=none; comparison_scope=none
50 | Electrical Design Basis Specification | nan | EDB-050 | Steady-state voltage drop at utilization equipment shall not exceed 5%. | 8.2.3 | nan | Steady-state voltage drop at utilization equipment shall not exceed 3%. | 0.66 | 7 | final=0.660; semantic=0.910; containment=0.000; fuzz=0.986; predicate_similarity=1.000; warnings=None; anchors=drop,exceed,state,steady,utilization,voltage; reference_object=drop,state,steady,utilization,voltage; comparison_object=drop,state,steady,utilization,voltage; reference_scope=none; comparison_scope=none
51 | Electrical Design Basis Specification | Safety | EDB-051 | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | 8.2.3 | nan | Steady-state voltage drop at utilization equipment shall not exceed 3%. | 0.466 | 8 | final=0.466; semantic=0.659; containment=0.000; fuzz=0.675; predicate_similarity=1.000; warnings=Borderline score; anchors=drop,exceed,voltage; reference_object=automatic,drop,during,motors,reacceleration,voltage; comparison_object=drop,state,steady,utilization,voltage; reference_scope=none; comparison_scope=none
75 | Electrical Design Basis Specification | Safety | EDB-075 | Substation alarms shall include transformer trip, breaker trip, and ground fault. | 8.2.4 | Safety | Substation alarms shall include transformer trip, breaker trip, ground fault, and fire alarm. | 0.655 | 9 | final=0.655; semantic=0.973; containment=0.000; fuzz=0.888; predicate_similarity=1.000; warnings=None; anchors=alarms,breaker,fault,substation,transformer,trip; reference_object=alarms,substation; comparison_object=alarms,substation; reference_scope=none; comparison_scope=none
64 | Electrical Design Basis Specification | Safety | EDB-064 | Standby generators shall be provided for critical loads. | 8.3.1 | Safety | Standby generators shall be provided for all critical process and safety loads. | 0.628 | 10 | final=0.628; semantic=0.948; containment=0.000; fuzz=0.830; predicate_similarity=1.000; warnings=None; anchors=critical,generators,loads,standby; reference_object=generators,standby; comparison_object=generators,standby; reference_scope=critical loads; comparison_scope=all critical process safety loads
55 | Electrical Design Basis Specification | Safety | EDB-055 | All electrical equipment shall be grounded and bonded to the plant grounding grid. | 8.3.2 | Safety | All PROJECT electrical equipment shall be grounded, bonded, and surge protected. | 0.531 | 11 | final=0.531; semantic=0.774; containment=0.000; fuzz=0.738; predicate_similarity=0.500; warnings=Low anchor overlap; anchors=bonded,grounded; reference_object=none; comparison_object=project; reference_scope=none; comparison_scope=none
71 | Electrical Design Basis Specification | nan | EDB-071 | Power and instrumentation cables shall be installed in separate tray systems. | 8.3.3 | nan | Power and instrumentation cables shall be installed in separate tray systems with 300 mm separation. | 0.625 | 12 | final=0.625; semantic=0.910; containment=0.000; fuzz=0.870; predicate_similarity=1.000; warnings=None; anchors=cables,installed,instrumentation,power,separate,tray; reference_object=cables,instrumentation,power; comparison_object=cables,instrumentation,power; reference_scope=none; comparison_scope=none
58 | Electrical Design Basis Specification | nan | EDB-058 | Transformer impedance shall be 5.75% nominal. | 8.4.1 | nan | Transformer impedance shall be 6.5% nominal. | 0.658 | 13 | final=0.658; semantic=0.922; containment=0.000; fuzz=0.966; predicate_similarity=1.000; warnings=None; anchors=impedance,nominal,transformer; reference_object=impedance,transformer; comparison_object=impedance,transformer; reference_scope=none; comparison_scope=none
63 | Electrical Design Basis Specification | Safety | EDB-063 | Automatic motor reacceleration shall occur in priority sequence after voltage restoration. | 8.4.2 | Safety | Automatic motor reacceleration shall occur in configurable priority sequence after voltage restoration. | 0.67 | 14 | final=0.670; semantic=0.975; containment=0.000; fuzz=0.933; predicate_similarity=1.000; warnings=None; anchors=after,automatic,motor,occur,priority,reacceleration,restoration,sequence,voltage; reference_object=automatic,motor,reacceleration; comparison_object=automatic,motor,reacceleration; reference_scope=none; comparison_scope=none
51 | Electrical Design Basis Specification | Safety | EDB-051 | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | 8.4.3 | Safety | The motor reacceleration study shall confirm that system voltage drop during automatic reacceleration of motors shall not exceed 10%. Motors shall be grouped by process priority, and each group shall be released only after bus voltage has recovered above the configured threshold. | 0.468 | 15 | final=0.468; semantic=0.830; containment=0.000; fuzz=0.453; predicate_similarity=1.000; warnings=Borderline score; anchors=automatic,drop,during,exceed,motors,reacceleration,voltage; reference_object=automatic,drop,during,motors,reacceleration,voltage; comparison_object=motor,reacceleration,study; reference_scope=none; comparison_scope=none
74 | Electrical Design Basis Specification | Cyber Security | EDB-074 | Protective relays shall communicate alarms to the substation HMI. | 8.4.4 | Cyber Security | Protective relays shall communicate alarms and events to the PROJECT substation HMI. | 0.645 | 16 | final=0.645; semantic=0.959; containment=0.000; fuzz=0.872; predicate_similarity=1.000; warnings=None; anchors=alarms,communicate,protective,relays,substation; reference_object=protective,relays; comparison_object=protective,relays; reference_scope=none; comparison_scope=none
66 | Electrical Design Basis Specification | Safety | EDB-066 | Automatic transfer switches shall be provided for emergency loads. | 8.5.1 | Safety | Automatic transfer switches with bypass isolation shall be provided for emergency loads. | 0.62 | 17 | final=0.620; semantic=0.906; containment=0.000; fuzz=0.857; predicate_similarity=1.000; warnings=None; anchors=automatic,emergency,loads,switches,transfer; reference_object=automatic,switches,transfer; comparison_object=automatic,bypass,isolation,switches,transfer; reference_scope=emergency loads; comparison_scope=emergency loads
69 | Electrical Design Basis Specification | Safety | EDB-069 | Cable glands in classified areas shall be explosion-proof rated. | 8.5.2 | Safety | Cable glands in classified areas shall be IEC certified explosion-proof rated. | 0.619 | 18 | final=0.619; semantic=0.873; containment=0.000; fuzz=0.901; predicate_similarity=1.000; warnings=None; anchors=areas,cable,classified,explosion,glands,proof,rated; reference_object=areas,cable,classified,glands; comparison_object=areas,cable,classified,glands; reference_scope=none; comparison_scope=none
54 | Electrical Design Basis Specification | Safety | EDB-054 | Explosion-proof equipment shall be used in Class I Division 1 locations. | 8.5.3 | Safety | Explosion-proof equipment shall be used in Zone 1 classified locations. | 0.589 | 19 | final=0.589; semantic=0.832; containment=0.000; fuzz=0.853; predicate_similarity=0.500; warnings=None; anchors=explosion,locations,proof,used; reference_object=explosion,proof; comparison_object=explosion,proof; reference_scope=none; comparison_scope=none
76 | Electrical Design Basis Specification | Cyber Security | EDB-076 | Electrical monitoring systems shall integrate with plant SCADA. | 8.5.4 | Cyber Security | Electrical monitoring systems shall integrate with PROJECT SCADA and historian. | 0.59 | 20 | final=0.590; semantic=0.842; containment=0.000; fuzz=0.845; predicate_similarity=0.667; warnings=None; anchors=integrate,monitoring,scada; reference_object=monitoring; comparison_object=monitoring; reference_scope=none; comparison_scope=none
61 | Electrical Design Basis Specification | Safety | EDB-061 | Each motor starter shall include a local disconnecting device. | 8.6.1 | Safety | Each motor starter shall include a lockable local disconnecting device. | 0.662 | 21 | final=0.662; semantic=0.956; containment=0.000; fuzz=0.932; predicate_similarity=1.000; warnings=None; anchors=disconnecting,each,local,motor,starter; reference_object=each,motor,starter; comparison_object=each,motor,starter; reference_scope=none; comparison_scope=none
52 | Electrical Design Basis Specification | Safety | EDB-052 | Electrical equipment short-circuit ratings shall exceed the maximum available fault current. | 8.6.2 | Safety | Electrical equipment short-circuit ratings shall exceed the maximum calculated fault current by 10%. | 0.634 | 22 | final=0.634; semantic=0.906; containment=0.000; fuzz=0.906; predicate_similarity=0.800; warnings=None; anchors=circuit,current,exceed,fault,maximum,ratings,short; reference_object=circuit,ratings,short; comparison_object=circuit,ratings,short; reference_scope=none; comparison_scope=none
65 | Electrical Design Basis Specification | nan | EDB-065 | Standby generators shall be diesel engine driven. | 8.6.3 | nan | Standby generators shall be gas turbine driven. | 0.592 | 23 | final=0.592; semantic=0.839; containment=0.000; fuzz=0.854; predicate_similarity=0.500; warnings=None; anchors=driven,generators,standby; reference_object=generators,standby; comparison_object=generators,standby; reference_scope=none; comparison_scope=none
59 | Electrical Design Basis Specification | nan | EDB-059 | Transformers shall have 65°C temperature rise with Class OA insulation. | 8.6.4 | nan | Transformers shall have 80°C temperature rise with Class F insulation. | 0.644 | 24 | final=0.644; semantic=0.897; containment=0.000; fuzz=0.950; predicate_similarity=1.000; warnings=None; anchors=class,have,insulation,rise,temperature,transformers; reference_object=transformers; comparison_object=transformers; reference_scope=none; comparison_scope=none
73 | Electrical Design Basis Specification | Safety | EDB-073 | Protective device coordination studies shall be performed. | 8.7.1 | Safety | Protective device coordination and arc flash studies shall be performed. | 0.554 | 25 | final=0.554; semantic=0.715; containment=0.000; fuzz=0.892; predicate_similarity=1.000; warnings=None; anchors=coordination,performed,protective,studies; reference_object=coordination,protective,studies; comparison_object=coordination,flash,protective,studies; reference_scope=none; comparison_scope=none
68 | Electrical Design Basis Specification | nan | EDB-068 | Wire and cable terminations at motors shall use compression lugs. | 8.7.2 | nan | Wire and cable terminations at motors shall use compression lugs with heat shrink boots. | 0.607 | 26 | final=0.607; semantic=0.881; containment=0.000; fuzz=0.850; predicate_similarity=1.000; warnings=None; anchors=cable,compression,lugs,motors,terminations,wire; reference_object=cable,motors,terminations,wire; comparison_object=cable,motors,terminations,wire; reference_scope=none; comparison_scope=none
56 | Electrical Design Basis Specification | Safety | EDB-056 | Arc flash warning labels shall be installed on energized equipment. | 8.7.3 | Safety | Arc flash warning labels and incident energy values shall be installed on energized equipment. | 0.606 | 27 | final=0.606; semantic=0.891; containment=0.000; fuzz=0.832; predicate_similarity=1.000; warnings=None; anchors=energized,flash,installed,labels,warning; reference_object=flash,labels,warning; comparison_object=energy,flash,incident,labels,values,warning; reference_scope=none; comparison_scope=none
70 | Electrical Design Basis Specification | nan | EDB-070 | Cable ampacity shall be derated for ambient temperature and grouping. | 8.7.4 | nan | Cable ampacity shall be derated for ambient temperature, grouping, and solar loading. | 0.629 | 28 | final=0.629; semantic=0.921; containment=0.000; fuzz=0.868; predicate_similarity=1.000; warnings=None; anchors=ambient,ampacity,cable,derated,grouping,temperature; reference_object=ampacity,cable; comparison_object=ampacity,cable; reference_scope=ambient temperature grouping; comparison_scope=ambient temperature
62 | Electrical Design Basis Specification | Safety | EDB-062 | Motor starters shall include overload, short-circuit, and phase-loss protection. | 8.7.5 | Safety | Motor starter protection shall include overload, short-circuit, phase-loss, and undervoltage protection. The protection settings shall be coordinated with upstream circuit breakers and documented in the protective device coordination study. | 0.49 | 29 | final=0.490; semantic=0.868; containment=0.000; fuzz=0.476; predicate_similarity=1.000; warnings=Borderline score; anchors=circuit,loss,motor,overload,phase,protection,short; reference_object=motor,starters; comparison_object=motor,protection,starter; reference_scope=none; comparison_scope=none
[5 empty] | 8.2.2 | nan | Motor starters shall be VFD type for motors above 100 hp unless otherwise specified.

## Diagnostics
Reference Source File | Reference Source Row | Reference Compare Text | Reference Indexed Description | Comparison Source File | Comparison Compare Text | Final Score | Semantic Score | Containment Score | Fuzzy Score | Predicate Similarity | Potential Issue | Reference Full Row
Electrical_Design_Basis_Company_Standard.xlsx | 10 | Power transformers shall be oil-filled ONAN type. | Power transformers shall be oil-filled ONAN type. | Electrical_Design_Basis_Project | Power transformers shall be dry-type cast resin transformers. | 0.4586 | 0.6419 | 0 | 0.6727 | 0.3333 | Borderline score | {'Tool Unique Code': 57, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-057', 'Requirement Text': 'Power transformers shall be oil-filled ONAN type.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 10, '_indexed_description': 'Power transformers shall be oil-filled ONAN type.', '_containment_keys': ['power transformers shall be oil-filled onan type.']}
Electrical_Design_Basis_Company_Standard.xlsx | 2 | Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution. | Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution. | Electrical_Design_Basis_Project | PROJECT nominal system voltages shall be 480 V, 6.6 kV, and 13.8 kV for low and medium voltage distribution. | 0.6572 | 0.9332 | 0 | 0.9463 | 1 | None | {'Tool Unique Code': 49, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-049', 'Requirement Text': 'Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 2, '_indexed_description': 'Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution.', '_containment_keys': ['nominal system voltages shall be 480 v 4.16 kv and 13.8 kv for low and medium voltage distribution.']}
Electrical_Design_Basis_Company_Standard.xlsx | 25 | Circuit breakers shall have minimum interrupting rating of 35 kA. | Circuit breakers shall have minimum interrupting rating of 35 kA. | Electrical_Design_Basis_Project | Circuit breakers shall have minimum interrupting rating of 50 kA. | 0.6688 | 0.9335 | 0 | 0.9846 | 1 | None | {'Tool Unique Code': 72, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-072', 'Requirement Text': 'Circuit breakers shall have minimum interrupting rating of 35 kA.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 25, '_indexed_description': 'Circuit breakers shall have minimum interrupting rating of 35 kA.', '_containment_keys': ['circuit breakers shall have minimum interrupting rating of 35 ka.']}
Electrical_Design_Basis_Company_Standard.xlsx | 6 | Equipment installed in classified locations shall comply with NFPA 70 requirements. | Equipment installed in classified locations shall comply with NFPA 70 requirements. | Electrical_Design_Basis_Project | Equipment installed in classified locations shall comply with IEC 60364 requirements. | 0.5371 | 0.6464 | 0 | 0.9286 | 0.5 | None | {'Tool Unique Code': 53, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-053', 'Requirement Text': 'Equipment installed in classified locations shall comply with NFPA 70 requirements.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 6, '_indexed_description': 'Equipment installed in classified locations shall comply with NFPA 70 requirements.', '_containment_keys': ['equipment installed in classified locations shall comply with nfpa 70 requirements.']}
Flow_Meter_Company_Standard.xlsx | 10 | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | Electrical_Design_Basis_Project | Equipment installed in classified locations shall comply with IEC 60364 requirements. | 0.4841 | 0.7251 | 0 | 0.6467 | 0.5 | Borderline score ¦ Low anchor overlap | {'Tool Unique Code': 29, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-029', 'Requirement Text': 'All electrical equipment installed in hazardous areas shall comply with IEC 60079.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 10, '_indexed_description': 'All electrical equipment installed in hazardous areas shall comply with IEC 60079.', '_containment_keys': ['all electrical equipment installed in hazardous areas shall comply with iec 60079.']}
Electrical_Design_Basis_Company_Standard.xlsx | 20 | Transfer to standby power shall occur within 30 seconds. | Transfer to standby power shall occur within 30 seconds. | Electrical_Design_Basis_Project | Transfer to standby power shall occur within 10 seconds. | 0.6829 | 0.9707 | 0 | 0.9821 | 1 | None | {'Tool Unique Code': 67, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-067', 'Requirement Text': 'Transfer to standby power shall occur within 30 seconds.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 20, '_indexed_description': 'Transfer to standby power shall occur within 30 seconds.', '_containment_keys': ['transfer to standby power shall occur within 30 seconds.']}
Electrical_Design_Basis_Company_Standard.xlsx | 3 | Steady-state voltage drop at utilization equipment shall not exceed 5%. | Steady-state voltage drop at utilization equipment shall not exceed 5%. | Electrical_Design_Basis_Project | Steady-state voltage drop at utilization equipment shall not exceed 3%. | 0.6596 | 0.9097 | 0 | 0.9859 | 1 | None | {'Tool Unique Code': 50, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-050', 'Requirement Text': 'Steady-state voltage drop at utilization equipment shall not exceed 5%.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 3, '_indexed_description': 'Steady-state voltage drop at utilization equipment shall not exceed 5%.', '_containment_keys': ['steady-state voltage drop at utilization equipment shall not exceed 5 .']}
Electrical_Design_Basis_Company_Standard.xlsx | 4 | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | Electrical_Design_Basis_Project | Steady-state voltage drop at utilization equipment shall not exceed 3%. | 0.4662 | 0.659 | 0 | 0.6753 | 1 | Borderline score | {'Tool Unique Code': 51, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-051', 'Requirement Text': 'System voltage drop during automatic reacceleration of motors shall not exceed 15%.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 4, '_indexed_description': 'System voltage drop during automatic reacceleration of motors shall not exceed 15%.', '_containment_keys': ['system voltage drop during automatic reacceleration of motors shall not exceed 15 .']}
Electrical_Design_Basis_Company_Standard.xlsx | 28 | Substation alarms shall include transformer trip, breaker trip, and ground fault. | Substation alarms shall include transformer trip, breaker trip, and ground fault. | Electrical_Design_Basis_Project | Substation alarms shall include transformer trip, breaker trip, ground fault, and fire alarm. | 0.6554 | 0.9728 | 0 | 0.8876 | 1 | None | {'Tool Unique Code': 75, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-075', 'Requirement Text': 'Substation alarms shall include transformer trip, breaker trip, and ground fault.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 28, '_indexed_description': 'Substation alarms shall include transformer trip, breaker trip, and ground fault.', '_containment_keys': ['substation alarms shall include transformer trip breaker trip and ground fault.']}
Electrical_Design_Basis_Company_Standard.xlsx | 17 | Standby generators shall be provided for critical loads. | Standby generators shall be provided for critical loads. | Electrical_Design_Basis_Project | Standby generators shall be provided for all critical process and safety loads. | 0.6281 | 0.948 | 0 | 0.8296 | 1 | None | {'Tool Unique Code': 64, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-064', 'Requirement Text': 'Standby generators shall be provided for critical loads.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 17, '_indexed_description': 'Standby generators shall be provided for critical loads.', '_containment_keys': ['standby generators shall be provided for critical loads.']}
Electrical_Design_Basis_Company_Standard.xlsx | 8 | All electrical equipment shall be grounded and bonded to the plant grounding grid. | All electrical equipment shall be grounded and bonded to the plant grounding grid. | Electrical_Design_Basis_Project | All PROJECT electrical equipment shall be grounded, bonded, and surge protected. | 0.5307 | 0.7736 | 0 | 0.7375 | 0.5 | Low anchor overlap | {'Tool Unique Code': 55, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-055', 'Requirement Text': 'All electrical equipment shall be grounded and bonded to the plant grounding grid.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 8, '_indexed_description': 'All electrical equipment shall be grounded and bonded to the plant grounding grid.', '_containment_keys': ['all electrical equipment shall be grounded and bonded to the plant grounding grid.']}
Electrical_Design_Basis_Company_Standard.xlsx | 24 | Power and instrumentation cables shall be installed in separate tray systems. | Power and instrumentation cables shall be installed in separate tray systems. | Electrical_Design_Basis_Project | Power and instrumentation cables shall be installed in separate tray systems with 300 mm separation. | 0.6252 | 0.9105 | 0 | 0.8701 | 1 | None | {'Tool Unique Code': 71, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-071', 'Requirement Text': 'Power and instrumentation cables shall be installed in separate tray systems.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 24, '_indexed_description': 'Power and instrumentation cables shall be installed in separate tray systems.', '_containment_keys': ['power and instrumentation cables shall be installed in separate tray systems.']}
Electrical_Design_Basis_Company_Standard.xlsx | 11 | Transformer impedance shall be 5.75% nominal. | Transformer impedance shall be 5.75% nominal. | Electrical_Design_Basis_Project | Transformer impedance shall be 6.5% nominal. | 0.6583 | 0.9216 | 0 | 0.9655 | 1 | None | {'Tool Unique Code': 58, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-058', 'Requirement Text': 'Transformer impedance shall be 5.75% nominal.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 11, '_indexed_description': 'Transformer impedance shall be 5.75% nominal.', '_containment_keys': ['transformer impedance shall be 5.75 nominal.']}
Electrical_Design_Basis_Company_Standard.xlsx | 16 | Automatic motor reacceleration shall occur in priority sequence after voltage restoration. | Automatic motor reacceleration shall occur in priority sequence after voltage restoration. | Electrical_Design_Basis_Project | Automatic motor reacceleration shall occur in configurable priority sequence after voltage restoration. | 0.6699 | 0.9753 | 0 | 0.9326 | 1 | None | {'Tool Unique Code': 63, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-063', 'Requirement Text': 'Automatic motor reacceleration shall occur in priority sequence after voltage restoration.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 16, '_indexed_description': 'Automatic motor reacceleration shall occur in priority sequence after voltage restoration.', '_containment_keys': ['automatic motor reacceleration shall occur in priority sequence after voltage restoration.']}
Electrical_Design_Basis_Company_Standard.xlsx | 4 | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | System voltage drop during automatic reacceleration of motors shall not exceed 15%. | Electrical_Design_Basis_Project | The motor reacceleration study shall confirm that system voltage drop during automatic reacceleration of motors shall not exceed 10%. Motors shall be grouped by process priority, and each group shall be released only after bus voltage has recovered above the configured threshold. | 0.4681 | 0.8304 | 0 | 0.453 | 1 | Borderline score | {'Tool Unique Code': 51, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-051', 'Requirement Text': 'System voltage drop during automatic reacceleration of motors shall not exceed 15%.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 4, '_indexed_description': 'System voltage drop during automatic reacceleration of motors shall not exceed 15%.', '_containment_keys': ['system voltage drop during automatic reacceleration of motors shall not exceed 15 .']}
Electrical_Design_Basis_Company_Standard.xlsx | 27 | Protective relays shall communicate alarms to the substation HMI. | Protective relays shall communicate alarms to the substation HMI. | Electrical_Design_Basis_Project | Protective relays shall communicate alarms and events to the PROJECT substation HMI. | 0.6453 | 0.959 | 0 | 0.8725 | 1 | None | {'Tool Unique Code': 74, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'EDB-074', 'Requirement Text': 'Protective relays shall communicate alarms to the substation HMI.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 27, '_indexed_description': 'Protective relays shall communicate alarms to the substation HMI.', '_containment_keys': ['protective relays shall communicate alarms to the substation hmi.']}
Electrical_Design_Basis_Company_Standard.xlsx | 19 | Automatic transfer switches shall be provided for emergency loads. | Automatic transfer switches shall be provided for emergency loads. | Electrical_Design_Basis_Project | Automatic transfer switches with bypass isolation shall be provided for emergency loads. | 0.6195 | 0.9059 | 0 | 0.8571 | 1 | None | {'Tool Unique Code': 66, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-066', 'Requirement Text': 'Automatic transfer switches shall be provided for emergency loads.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 19, '_indexed_description': 'Automatic transfer switches shall be provided for emergency loads.', '_containment_keys': ['automatic transfer switches shall be provided for emergency loads.']}
Electrical_Design_Basis_Company_Standard.xlsx | 22 | Cable glands in classified areas shall be explosion-proof rated. | Cable glands in classified areas shall be explosion-proof rated. | Electrical_Design_Basis_Project | Cable glands in classified areas shall be IEC certified explosion-proof rated. | 0.6195 | 0.8727 | 0 | 0.9014 | 1 | None | {'Tool Unique Code': 69, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-069', 'Requirement Text': 'Cable glands in classified areas shall be explosion-proof rated.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 22, '_indexed_description': 'Cable glands in classified areas shall be explosion-proof rated.', '_containment_keys': ['cable glands in classified areas shall be explosion-proof rated.']}
Electrical_Design_Basis_Company_Standard.xlsx | 7 | Explosion-proof equipment shall be used in Class I Division 1 locations. | Explosion-proof equipment shall be used in Class I Division 1 locations. | Electrical_Design_Basis_Project | Explosion-proof equipment shall be used in Zone 1 classified locations. | 0.5887 | 0.8318 | 0 | 0.8531 | 0.5 | None | {'Tool Unique Code': 54, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-054', 'Requirement Text': 'Explosion-proof equipment shall be used in Class I Division 1 locations.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 7, '_indexed_description': 'Explosion-proof equipment shall be used in Class I Division 1 locations.', '_containment_keys': ['explosion-proof equipment shall be used in class i division 1 locations.']}
Electrical_Design_Basis_Company_Standard.xlsx | 29 | Electrical monitoring systems shall integrate with plant SCADA. | Electrical monitoring systems shall integrate with plant SCADA. | Electrical_Design_Basis_Project | Electrical monitoring systems shall integrate with PROJECT SCADA and historian. | 0.5903 | 0.842 | 0 | 0.8451 | 0.6667 | None | {'Tool Unique Code': 76, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'EDB-076', 'Requirement Text': 'Electrical monitoring systems shall integrate with plant SCADA.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 29, '_indexed_description': 'Electrical monitoring systems shall integrate with plant SCADA.', '_containment_keys': ['electrical monitoring systems shall integrate with plant scada.']}
Electrical_Design_Basis_Company_Standard.xlsx | 14 | Each motor starter shall include a local disconnecting device. | Each motor starter shall include a local disconnecting device. | Electrical_Design_Basis_Project | Each motor starter shall include a lockable local disconnecting device. | 0.6621 | 0.9561 | 0 | 0.9323 | 1 | None | {'Tool Unique Code': 61, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-061', 'Requirement Text': 'Each motor starter shall include a local disconnecting device.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 14, '_indexed_description': 'Each motor starter shall include a local disconnecting device.', '_containment_keys': ['each motor starter shall include a local disconnecting device.']}
Electrical_Design_Basis_Company_Standard.xlsx | 5 | Electrical equipment short-circuit ratings shall exceed the maximum available fault current. | Electrical equipment short-circuit ratings shall exceed the maximum available fault current. | Electrical_Design_Basis_Project | Electrical equipment short-circuit ratings shall exceed the maximum calculated fault current by 10%. | 0.6342 | 0.9057 | 0 | 0.9062 | 0.8 | None | {'Tool Unique Code': 52, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-052', 'Requirement Text': 'Electrical equipment short-circuit ratings shall exceed the maximum available fault current.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 5, '_indexed_description': 'Electrical equipment short-circuit ratings shall exceed the maximum available fault current.', '_containment_keys': ['electrical equipment short-circuit ratings shall exceed the maximum available fault current.']}
Electrical_Design_Basis_Company_Standard.xlsx | 18 | Standby generators shall be diesel engine driven. | Standby generators shall be diesel engine driven. | Electrical_Design_Basis_Project | Standby generators shall be gas turbine driven. | 0.5919 | 0.8392 | 0 | 0.8542 | 0.5 | None | {'Tool Unique Code': 65, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-065', 'Requirement Text': 'Standby generators shall be diesel engine driven.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 18, '_indexed_description': 'Standby generators shall be diesel engine driven.', '_containment_keys': ['standby generators shall be diesel engine driven.']}
Electrical_Design_Basis_Company_Standard.xlsx | 12 | Transformers shall have 65°C temperature rise with Class OA insulation. | Transformers shall have 65°C temperature rise with Class OA insulation. | Electrical_Design_Basis_Project | Transformers shall have 80°C temperature rise with Class F insulation. | 0.644 | 0.8973 | 0 | 0.9504 | 1 | None | {'Tool Unique Code': 59, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-059', 'Requirement Text': 'Transformers shall have 65°C temperature rise with Class OA insulation.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 12, '_indexed_description': 'Transformers shall have 65°C temperature rise with Class OA insulation.', '_containment_keys': ['transformers shall have 65 c temperature rise with class oa insulation.']}
Electrical_Design_Basis_Company_Standard.xlsx | 26 | Protective device coordination studies shall be performed. | Protective device coordination studies shall be performed. | Electrical_Design_Basis_Project | Protective device coordination and arc flash studies shall be performed. | 0.5535 | 0.7146 | 0 | 0.8923 | 1 | None | {'Tool Unique Code': 73, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-073', 'Requirement Text': 'Protective device coordination studies shall be performed.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 26, '_indexed_description': 'Protective device coordination studies shall be performed.', '_containment_keys': ['protective device coordination studies shall be performed.']}
Electrical_Design_Basis_Company_Standard.xlsx | 21 | Wire and cable terminations at motors shall use compression lugs. | Wire and cable terminations at motors shall use compression lugs. | Electrical_Design_Basis_Project | Wire and cable terminations at motors shall use compression lugs with heat shrink boots. | 0.6074 | 0.8813 | 0 | 0.8497 | 1 | None | {'Tool Unique Code': 68, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-068', 'Requirement Text': 'Wire and cable terminations at motors shall use compression lugs.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 21, '_indexed_description': 'Wire and cable terminations at motors shall use compression lugs.', '_containment_keys': ['wire and cable terminations at motors shall use compression lugs.']}
Electrical_Design_Basis_Company_Standard.xlsx | 9 | Arc flash warning labels shall be installed on energized equipment. | Arc flash warning labels shall be installed on energized equipment. | Electrical_Design_Basis_Project | Arc flash warning labels and incident energy values shall be installed on energized equipment. | 0.606 | 0.8908 | 0 | 0.8323 | 1 | None | {'Tool Unique Code': 56, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-056', 'Requirement Text': 'Arc flash warning labels shall be installed on energized equipment.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 9, '_indexed_description': 'Arc flash warning labels shall be installed on energized equipment.', '_containment_keys': ['arc flash warning labels shall be installed on energized equipment.']}
Electrical_Design_Basis_Company_Standard.xlsx | 23 | Cable ampacity shall be derated for ambient temperature and grouping. | Cable ampacity shall be derated for ambient temperature and grouping. | Electrical_Design_Basis_Project | Cable ampacity shall be derated for ambient temperature, grouping, and solar loading. | 0.6291 | 0.9214 | 0 | 0.8684 | 1 | None | {'Tool Unique Code': 70, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': nan, 'Requirement ID': 'EDB-070', 'Requirement Text': 'Cable ampacity shall be derated for ambient temperature and grouping.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 23, '_indexed_description': 'Cable ampacity shall be derated for ambient temperature and grouping.', '_containment_keys': ['cable ampacity shall be derated for ambient temperature and grouping.']}
Electrical_Design_Basis_Company_Standard.xlsx | 15 | Motor starters shall include overload, short-circuit, and phase-loss protection. | Motor starters shall include overload, short-circuit, and phase-loss protection. | Electrical_Design_Basis_Project | Motor starter protection shall include overload, short-circuit, phase-loss, and undervoltage protection. The protection settings shall be coordinated with upstream circuit breakers and documented in the protective device coordination study. | 0.4902 | 0.8683 | 0 | 0.4762 | 1 | Borderline score | {'Tool Unique Code': 62, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-062', 'Requirement Text': 'Motor starters shall include overload, short-circuit, and phase-loss protection.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 15, '_indexed_description': 'Motor starters shall include overload, short-circuit, and phase-loss protection.', '_containment_keys': ['motor starters shall include overload short-circuit and phase-loss protection.']}

## Run Summary
Metric | Value
Comparison File | Electrical_Design_Basis_Project
Reference Dataset Name | Reference Dataset
Comparison Dataset Name | Comparison Dataset
Reference Compare Column | Requirement Text
Comparison Compare Column | Requirement Text
Description Confidence Score | 196
Total Comparison Rows | 28
Matched Comparison Rows | 27
Unmatched Comparison Rows | 1
Output Rows | 30
Processing Mode | matches_only
Semantic Threshold | 0.55
Final Score Threshold | 0.44

## Platform Info
Item | Value
Platform | darwin
Excel COM Redline Available | No
Mac Rich Text Redline Available | Yes
Note | Windows uses Excel COM redline. Mac/non-Windows uses XlsxWriter rich text when available.