## Results
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text | Comparison Dataset - Requirement ID | Special Code | Comparison Dataset - Requirement Text | Score | Match Rank | Match Diagnostics
49 | Electrical Design Basis Specification | nan | EDB-049 | Nominal system voltages shall be 480 V, 4.16 kV, and 13.8 kV for low and medium voltage distribution.
50 | Electrical Design Basis Specification | nan | EDB-050 | Steady-state voltage drop at utilization equipment shall not exceed 5%.
51 | Electrical Design Basis Specification | Safety | EDB-051 | System voltage drop during automatic reacceleration of motors shall not exceed 15%.
52 | Electrical Design Basis Specification | Safety | EDB-052 | Electrical equipment short-circuit ratings shall exceed the maximum available fault current.
53 | Electrical Design Basis Specification | Safety | EDB-053 | Equipment installed in classified locations shall comply with NFPA 70 requirements.
54 | Electrical Design Basis Specification | Safety | EDB-054 | Explosion-proof equipment shall be used in Class I Division 1 locations.
55 | Electrical Design Basis Specification | Safety | EDB-055 | All electrical equipment shall be grounded and bonded to the plant grounding grid. | 6.5.3 | Safety | All meter station equipment shall be grounded, bonded, and surge protected. | 0.508 | 2 | final=0.508; semantic=0.758; containment=0.000; fuzz=0.684; predicate_similarity=0.500; warnings=Borderline score ¦ Low anchor overlap; anchors=bonded,grounded; reference_object=none; comparison_object=meter,station; reference_scope=none; comparison_scope=none
56 | Electrical Design Basis Specification | Safety | EDB-056 | Arc flash warning labels shall be installed on energized equipment.
57 | Electrical Design Basis Specification | nan | EDB-057 | Power transformers shall be oil-filled ONAN type.
58 | Electrical Design Basis Specification | nan | EDB-058 | Transformer impedance shall be 5.75% nominal.
59 | Electrical Design Basis Specification | nan | EDB-059 | Transformers shall have 65°C temperature rise with Class OA insulation.
60 | Electrical Design Basis Specification | nan | EDB-060 | Motor starters shall be across-the-line type unless otherwise specified.
61 | Electrical Design Basis Specification | Safety | EDB-061 | Each motor starter shall include a local disconnecting device.
62 | Electrical Design Basis Specification | Safety | EDB-062 | Motor starters shall include overload, short-circuit, and phase-loss protection.
63 | Electrical Design Basis Specification | Safety | EDB-063 | Automatic motor reacceleration shall occur in priority sequence after voltage restoration.
64 | Electrical Design Basis Specification | Safety | EDB-064 | Standby generators shall be provided for critical loads.
65 | Electrical Design Basis Specification | nan | EDB-065 | Standby generators shall be diesel engine driven.
66 | Electrical Design Basis Specification | Safety | EDB-066 | Automatic transfer switches shall be provided for emergency loads.
67 | Electrical Design Basis Specification | nan | EDB-067 | Transfer to standby power shall occur within 30 seconds.
68 | Electrical Design Basis Specification | nan | EDB-068 | Wire and cable terminations at motors shall use compression lugs.
69 | Electrical Design Basis Specification | Safety | EDB-069 | Cable glands in classified areas shall be explosion-proof rated.
70 | Electrical Design Basis Specification | nan | EDB-070 | Cable ampacity shall be derated for ambient temperature and grouping.
71 | Electrical Design Basis Specification | nan | EDB-071 | Power and instrumentation cables shall be installed in separate tray systems.
72 | Electrical Design Basis Specification | Safety | EDB-072 | Circuit breakers shall have minimum interrupting rating of 35 kA.
73 | Electrical Design Basis Specification | Safety | EDB-073 | Protective device coordination studies shall be performed.
74 | Electrical Design Basis Specification | Cyber Security | EDB-074 | Protective relays shall communicate alarms to the substation HMI.
75 | Electrical Design Basis Specification | Safety | EDB-075 | Substation alarms shall include transformer trip, breaker trip, and ground fault.
76 | Electrical Design Basis Specification | Cyber Security | EDB-076 | Electrical monitoring systems shall integrate with plant SCADA.
21 | Liquid Custody Transfer Specification | nan | FM-021 | The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions. | 6.1.2 | nan | The PROJECT crude receipt metering facility shall be designed for continuous custody transfer measurement during all operating scenarios. | 0.556 | 1 | final=0.556; semantic=0.795; containment=0.000; fuzz=0.794; predicate_similarity=0.571; warnings=None; anchors=continuous,custody,during,facility,measurement,metering,operating,transfer; reference_object=custody,facility,metering,transfer; comparison_object=crude,facility,metering,project,receipt; reference_scope=continuous liquid hydrocarbon measurement during all operating conditions; comparison_scope=continuous custody transfer measurement during all operating scenarios
22 | Liquid Custody Transfer Specification | nan | FM-022 | Verification meters shall be provided to confirm primary meter performance. | 6.3.2 | nan | Verification ultrasonic meters shall be provided to validate primary meter performance. | 0.584 | 1 | final=0.584; semantic=0.820; containment=0.000; fuzz=0.852; predicate_similarity=0.750; warnings=None; anchors=meter,meters,performance,primary,verification; reference_object=meters,verification; comparison_object=meters,ultrasonic,verification; reference_scope=none; comparison_scope=none
23 | Liquid Custody Transfer Specification | nan | FM-023 | The metering system shall operate over a flow range of 20% to 100% of design flow. | 6.5.1 | nan | The metering system shall operate over a flow range of 10% to 100% of design flow. | 0.692 | 1 | final=0.692; semantic=0.989; containment=0.000; fuzz=0.988; predicate_similarity=1.000; warnings=None; anchors=flow,metering,operate,over,range; reference_object=metering; comparison_object=metering; reference_scope=none; comparison_scope=none
24 | Liquid Custody Transfer Specification | nan | FM-024 | Overall measurement uncertainty shall not exceed ±0.25% of indicated volume. | 6.2.2 | nan | Overall measurement uncertainty shall not exceed ±0.15% of indicated volume. | 0.69 | 1 | final=0.690; semantic=0.985; containment=0.000; fuzz=0.986; predicate_similarity=1.000; warnings=None; anchors=exceed,indicated,measurement,overall,uncertainty,volume; reference_object=measurement,overall,uncertainty; comparison_object=measurement,overall,uncertainty; reference_scope=none; comparison_scope=none
25 | Liquid Custody Transfer Specification | nan | FM-025 | All custody transfer meters, provers, and flow computers shall include locks or tamper seals. | 6.5.4 | nan | All custody transfer meters, provers, and flow computers shall include locks, tamper seals, or electronic access control. | 0.645 | 1 | final=0.645; semantic=0.979; containment=0.000; fuzz=0.846; predicate_similarity=1.000; warnings=None; anchors=computers,custody,flow,locks,meters,provers,seals,tamper,transfer; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none
26 | Liquid Custody Transfer Specification | Cyber Security | FM-026 | Electronic access to flow computers shall require authenticated user credentials. | 6.1.4 | Cyber Security | Electronic access to flow computers shall require multi-factor authenticated credentials. | 0.638 | 1 | final=0.638; semantic=0.924; containment=0.000; fuzz=0.894; predicate_similarity=0.750; warnings=None; anchors=access,authenticated,computers,credentials,electronic,flow,require; reference_object=access,computers,electronic,flow; comparison_object=access,computers,electronic,flow; reference_scope=none; comparison_scope=none
27 | Liquid Custody Transfer Specification | Cyber Security | FM-027 | All metering parameter changes shall be recorded in an audit log. | 6.4.2 | Cyber Security | All metering parameter changes shall be recorded in a secure audit log with timestamps. | 0.623 | 1 | final=0.623; semantic=0.926; containment=0.000; fuzz=0.842; predicate_similarity=1.000; warnings=None; anchors=audit,changes,metering,parameter,recorded; reference_object=changes,metering,parameter; comparison_object=changes,metering,parameter; reference_scope=none; comparison_scope=none
28 | Liquid Custody Transfer Specification | Cyber Security | FM-028 | Calibration settings shall be password protected. | 6.6.4 | Cyber Security | Calibration settings shall be password protected and limited to administrator accounts. | 0.594 | 1 | final=0.594; semantic=0.945; containment=0.000; fuzz=0.721; predicate_similarity=1.000; warnings=None; anchors=calibration,password,protected,settings; reference_object=calibration,settings; comparison_object=calibration,settings; reference_scope=none; comparison_scope=none
29 | Liquid Custody Transfer Specification | Safety | FM-029 | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | 6.3.1 | Safety | All electrical equipment installed in hazardous areas shall comply with NEMA 250 and project hazardous area classification requirements. | 0.468 | 1 | final=0.468; semantic=0.647; containment=0.000; fuzz=0.697; predicate_similarity=0.500; warnings=Borderline score; anchors=areas,comply,hazardous,installed; reference_object=areas,hazardous,installed; comparison_object=areas,hazardous,installed; reference_scope=none; comparison_scope=none
30 | Liquid Custody Transfer Specification | Safety | FM-030 | Intrinsic safety barriers shall be provided for field instrumentation in classified areas. | 6.7.3 | Safety | Redundant intrinsic safety barriers shall be provided for field instrumentation in classified areas. | 0.962 | 1 | final=0.962; semantic=0.944; containment=1.000; fuzz=0.947; predicate_similarity=1.000; warnings=None; anchors=areas,barriers,classified,field,instrumentation,intrinsic,safety; reference_object=barriers,intrinsic,safety; comparison_object=barriers,intrinsic,redundant,safety; reference_scope=field instrumentation classified; comparison_scope=field instrumentation classified
31 | Liquid Custody Transfer Specification | Safety | FM-031 | All meter station equipment shall be properly grounded and bonded. | 6.5.3 | Safety | All meter station equipment shall be grounded, bonded, and surge protected. | 0.606 | 1 | final=0.606; semantic=0.921; containment=0.000; fuzz=0.791; predicate_similarity=0.667; warnings=None; anchors=bonded,grounded,meter,station; reference_object=meter,station; comparison_object=meter,station; reference_scope=none; comparison_scope=none
32 | Liquid Custody Transfer Specification | nan | FM-032 | Meter stations shall allow safe access for operation and maintenance.
33 | Liquid Custody Transfer Specification | nan | FM-033 | A minimum upstream straight pipe length of 10 diameters shall be provided. | 6.1.1 | nan | A minimum upstream straight pipe length of 20 diameters shall be provided. | 0.675 | 1 | final=0.675; semantic=0.948; containment=0.000; fuzz=0.986; predicate_similarity=1.000; warnings=None; anchors=diameters,length,minimum,pipe,straight,upstream; reference_object=diameters,length,minimum,pipe,straight,upstream; comparison_object=diameters,length,minimum,pipe,straight,upstream; reference_scope=none; comparison_scope=none
34 | Liquid Custody Transfer Specification | nan | FM-034 | A minimum downstream straight pipe length of 5 diameters shall be provided. | 6.6.2 | nan | A minimum downstream straight pipe length of 10 diameters shall be provided. | 0.665 | 1 | final=0.665; semantic=0.928; containment=0.000; fuzz=0.980; predicate_similarity=1.000; warnings=None; anchors=diameters,downstream,length,minimum,pipe,straight; reference_object=diameters,downstream,length,minimum,pipe,straight; comparison_object=diameters,downstream,length,minimum,pipe,straight; reference_scope=none; comparison_scope=none
35 | Liquid Custody Transfer Specification | nan | FM-035 | Meter headers shall be designed to minimize flow disturbances. | 6.2.3 | nan | Meter headers shall be designed to eliminate swirl and flow disturbances. | 0.628 | 1 | final=0.628; semantic=0.925; containment=0.000; fuzz=0.859; predicate_similarity=0.667; warnings=None; anchors=disturbances,flow,headers,meter; reference_object=headers,meter; comparison_object=headers,meter; reference_scope=none; comparison_scope=none
36 | Liquid Custody Transfer Specification | Safety | FM-036 | Isolation valves shall be installed upstream and downstream of each meter. | 6.4.3 | Safety | Full-port isolation valves shall be installed upstream and downstream of each meter. | 0.957 | 1 | final=0.957; semantic=0.940; containment=1.000; fuzz=0.937; predicate_similarity=1.000; warnings=None; anchors=downstream,each,installed,isolation,meter,upstream; reference_object=isolation; comparison_object=full,isolation,port; reference_scope=none; comparison_scope=none
37 | Liquid Custody Transfer Specification | Safety | FM-037 | Double block and bleed isolation shall be provided for prover connections. | 6.7.2 | Safety | Double block and bleed isolation shall be provided for prover and calibration connections. | 0.646 | 1 | final=0.646; semantic=0.937; containment=0.000; fuzz=0.902; predicate_similarity=1.000; warnings=None; anchors=bleed,block,connections,double,isolation,prover; reference_object=bleed,block,double,isolation; comparison_object=bleed,block,double,isolation; reference_scope=prover connections; comparison_scope=prover calibration connections
38 | Liquid Custody Transfer Specification | nan | FM-038 | Meter bypass lines shall remain sealed closed during normal operation. | 6.3.3 | nan | Meter bypass lines shall remain locked and sealed closed during normal operation. | 0.667 | 1 | final=0.667; semantic=0.972; containment=0.000; fuzz=0.927; predicate_similarity=1.000; warnings=None; anchors=bypass,closed,during,meter,normal,operation,remain,sealed; reference_object=bypass,meter; comparison_object=bypass,meter; reference_scope=none; comparison_scope=none
39 | Liquid Custody Transfer Specification | Environmental | FM-039 | Drain connections shall discharge to a closed drain system.
40 | Liquid Custody Transfer Specification | Environmental | FM-040 | Fill connections shall permit safe priming of meter runs. | 6.6.3 | Environmental | Fill connections shall permit safe meter run priming and flushing. | 0.602 | 1 | final=0.602; semantic=0.931; containment=0.000; fuzz=0.764; predicate_similarity=0.800; warnings=None; anchors=connections,fill,meter,permit,priming,safe; reference_object=connections,fill; comparison_object=connections,fill; reference_scope=none; comparison_scope=none
41 | Liquid Custody Transfer Specification | Environmental | FM-041 | Blowdown connections shall route fluids to a closed recovery system. | 6.5.2 | Environmental | Blowdown connections shall route hydrocarbons to a vapor recovery system. | 0.539 | 1 | final=0.539; semantic=0.719; containment=0.000; fuzz=0.837; predicate_similarity=0.500; warnings=None; anchors=blowdown,connections,recovery,route; reference_object=blowdown,connections; comparison_object=blowdown,connections; reference_scope=none; comparison_scope=none
42 | Liquid Custody Transfer Specification | nan | FM-042 | Pressure transmitters shall have an accuracy of ±0.1% of span. | 6.2.4 | nan | Dual redundant pressure transmitters shall have an accuracy of ±0.05% of span. | 0.608 | 1 | final=0.608; semantic=0.870; containment=0.000; fuzz=0.868; predicate_similarity=1.000; warnings=None; anchors=accuracy,have,pressure,span,transmitters; reference_object=pressure,transmitters; comparison_object=dual,pressure,redundant,transmitters; reference_scope=none; comparison_scope=none
43 | Liquid Custody Transfer Specification | nan | FM-043 | Temperature sensing elements shall be RTDs with accuracy of ±0.2°C. | 6.4.4 | nan | Temperature sensing elements shall be dual RTDs with accuracy of ±0.1°C. | 0.665 | 1 | final=0.665; semantic=0.951; containment=0.000; fuzz=0.949; predicate_similarity=1.000; warnings=None; anchors=accuracy,elements,rtds,sensing,temperature; reference_object=elements,sensing,temperature; comparison_object=elements,sensing,temperature; reference_scope=none; comparison_scope=none
44 | Liquid Custody Transfer Specification | Cyber Security | FM-044 | A dedicated flow computer shall perform custody transfer calculations. | 6.6.1 | Cyber Security | A redundant flow computer pair shall perform custody transfer calculations. The flow computer configuration shall support role-based access, secure parameter downloads, and event transfer to the metering workstation. | 0.459 | 1 | final=0.459; semantic=0.805; containment=0.000; fuzz=0.458; predicate_similarity=1.000; warnings=Borderline score; anchors=calculations,computer,custody,flow,perform,transfer; reference_object=computer,dedicated,flow; comparison_object=computer,flow,pair,redundant; reference_scope=none; comparison_scope=none
45 | Liquid Custody Transfer Specification | nan | FM-045 | Critical measurement signals shall use redundant signal paths. | 6.7.4 | nan | Critical measurement signals shall use dual redundant signal paths. | 0.681 | 1 | final=0.681; semantic=0.981; containment=0.000; fuzz=0.961; predicate_similarity=1.000; warnings=None; anchors=critical,measurement,paths,redundant,signal,signals; reference_object=critical,measurement,signals; comparison_object=critical,measurement,signals; reference_scope=none; comparison_scope=none
46 | Liquid Custody Transfer Specification | nan | FM-046 | Metering data shall be archived in the facility historian. | 6.7.1 | nan | Metering data shall be archived in the PROJECT historian and backup server. | 0.583 | 1 | final=0.583; semantic=0.870; containment=0.000; fuzz=0.782; predicate_similarity=0.667; warnings=None; anchors=archived,data,historian,metering; reference_object=data,metering; comparison_object=data,metering; reference_scope=none; comparison_scope=none
47 | Liquid Custody Transfer Specification | nan | FM-047 | Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8. | 6.1.3 | nan | Flow meters shall be calibrated prior to commissioning per ISO 17089. | 0.607 | 1 | final=0.607; semantic=0.874; containment=0.000; fuzz=0.859; predicate_similarity=0.750; warnings=None; anchors=calibrated,commissioning,flow,meters,prior; reference_object=flow,meters; comparison_object=flow,meters; reference_scope=none; comparison_scope=none
48 | Liquid Custody Transfer Specification | nan | FM-048 | Custody transfer meters shall be verified every 6 months. | 6.4.1 | nan | Custody transfer meters shall be verified every 3 months. | 0.689 | 1 | final=0.689; semantic=0.986; containment=0.000; fuzz=0.982; predicate_similarity=1.000; warnings=None; anchors=custody,every,meters,months,transfer,verified; reference_object=custody,meters,transfer; comparison_object=custody,meters,transfer; reference_scope=none; comparison_scope=none
[5 empty] | 6.2.1 | Environmental | Drain and liquid handling connections shall be designed as a closed system. Drain connections shall discharge to the oily water closed drain system, fill connections shall permit safe meter run priming and flushing, and blowdown connections shall route hydrocarbons to a vapor recovery system.
[5 empty] | 6.7.5 | nan | The meter station layout shall support operation, maintenance, and proving activities. Meter stations shall allow safe operator access and maintenance clearance around meters, prover connections, isolation valves, drains, and instrument enclosures.

## Diagnostics
Reference Source File | Reference Source Row | Reference Compare Text | Reference Indexed Description | Comparison Source File | Comparison Compare Text | Final Score | Semantic Score | Containment Score | Fuzzy Score | Predicate Similarity | Potential Issue | Reference Full Row
Flow_Meter_Company_Standard.xlsx | 14 | A minimum upstream straight pipe length of 10 diameters shall be provided. | A minimum upstream straight pipe length of 10 diameters shall be provided. | Flow_Meter_Project | A minimum upstream straight pipe length of 20 diameters shall be provided. | 0.6753 | 0.9485 | 0 | 0.9865 | 1 | None | {'Tool Unique Code': 33, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-033', 'Requirement Text': 'A minimum upstream straight pipe length of 10 diameters shall be provided.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 14, '_indexed_description': 'A minimum upstream straight pipe length of 10 diameters shall be provided.', '_containment_keys': ['a minimum upstream straight pipe length of 10 diameters shall be provided.']}
Flow_Meter_Company_Standard.xlsx | 2 | The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions. | The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions. | Flow_Meter_Project | The PROJECT crude receipt metering facility shall be designed for continuous custody transfer measurement during all operating scenarios. | 0.5562 | 0.7949 | 0 | 0.7941 | 0.5714 | None | {'Tool Unique Code': 21, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-021', 'Requirement Text': 'The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 2, '_indexed_description': 'The custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions.', '_containment_keys': ['the custody transfer metering facility shall be designed for continuous liquid hydrocarbon measurement during all operating conditions.']}
Flow_Meter_Company_Standard.xlsx | 28 | Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8. | Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8. | Flow_Meter_Project | Flow meters shall be calibrated prior to commissioning per ISO 17089. | 0.6071 | 0.8735 | 0 | 0.8591 | 0.75 | None | {'Tool Unique Code': 47, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-047', 'Requirement Text': 'Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 28, '_indexed_description': 'Flow meters shall be calibrated prior to commissioning per API MPMS Chapter 5.8.', '_containment_keys': ['flow meters shall be calibrated prior to commissioning per api mpms chapter 5.8.']}
Flow_Meter_Company_Standard.xlsx | 7 | Electronic access to flow computers shall require authenticated user credentials. | Electronic access to flow computers shall require authenticated user credentials. | Flow_Meter_Project | Electronic access to flow computers shall require multi-factor authenticated credentials. | 0.638 | 0.9243 | 0 | 0.8941 | 0.75 | None | {'Tool Unique Code': 26, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FM-026', 'Requirement Text': 'Electronic access to flow computers shall require authenticated user credentials.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 7, '_indexed_description': 'Electronic access to flow computers shall require authenticated user credentials.', '_containment_keys': ['electronic access to flow computers shall require authenticated user credentials.']}
Flow_Meter_Company_Standard.xlsx | 5 | Overall measurement uncertainty shall not exceed ±0.25% of indicated volume. | Overall measurement uncertainty shall not exceed ±0.25% of indicated volume. | Flow_Meter_Project | Overall measurement uncertainty shall not exceed ±0.15% of indicated volume. | 0.6898 | 0.9847 | 0 | 0.9865 | 1 | None | {'Tool Unique Code': 24, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-024', 'Requirement Text': 'Overall measurement uncertainty shall not exceed ±0.25% of indicated volume.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 5, '_indexed_description': 'Overall measurement uncertainty shall not exceed ±0.25% of indicated volume.', '_containment_keys': ['overall measurement uncertainty shall not exceed 0.25 of indicated volume.']}
Flow_Meter_Company_Standard.xlsx | 16 | Meter headers shall be designed to minimize flow disturbances. | Meter headers shall be designed to minimize flow disturbances. | Flow_Meter_Project | Meter headers shall be designed to eliminate swirl and flow disturbances. | 0.6276 | 0.9245 | 0 | 0.8593 | 0.6667 | None | {'Tool Unique Code': 35, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-035', 'Requirement Text': 'Meter headers shall be designed to minimize flow disturbances.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 16, '_indexed_description': 'Meter headers shall be designed to minimize flow disturbances.', '_containment_keys': ['meter headers shall be designed to minimize flow disturbances.']}
Flow_Meter_Company_Standard.xlsx | 23 | Pressure transmitters shall have an accuracy of ±0.1% of span. | Pressure transmitters shall have an accuracy of ±0.1% of span. | Flow_Meter_Project | Dual redundant pressure transmitters shall have an accuracy of ±0.05% of span. | 0.6082 | 0.8698 | 0 | 0.8676 | 1 | None | {'Tool Unique Code': 42, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-042', 'Requirement Text': 'Pressure transmitters shall have an accuracy of ±0.1% of span.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 23, '_indexed_description': 'Pressure transmitters shall have an accuracy of ±0.1% of span.', '_containment_keys': ['pressure transmitters shall have an accuracy of 0.1 of span.']}
Flow_Meter_Company_Standard.xlsx | 10 | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | All electrical equipment installed in hazardous areas shall comply with IEC 60079. | Flow_Meter_Project | All electrical equipment installed in hazardous areas shall comply with NEMA 250 and project hazardous area classification requirements. | 0.468 | 0.647 | 0 | 0.6972 | 0.5 | Borderline score | {'Tool Unique Code': 29, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-029', 'Requirement Text': 'All electrical equipment installed in hazardous areas shall comply with IEC 60079.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 10, '_indexed_description': 'All electrical equipment installed in hazardous areas shall comply with IEC 60079.', '_containment_keys': ['all electrical equipment installed in hazardous areas shall comply with iec 60079.']}
Flow_Meter_Company_Standard.xlsx | 3 | Verification meters shall be provided to confirm primary meter performance. | Verification meters shall be provided to confirm primary meter performance. | Flow_Meter_Project | Verification ultrasonic meters shall be provided to validate primary meter performance. | 0.5837 | 0.8203 | 0 | 0.8519 | 0.75 | None | {'Tool Unique Code': 22, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-022', 'Requirement Text': 'Verification meters shall be provided to confirm primary meter performance.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 3, '_indexed_description': 'Verification meters shall be provided to confirm primary meter performance.', '_containment_keys': ['verification meters shall be provided to confirm primary meter performance.']}
Flow_Meter_Company_Standard.xlsx | 19 | Meter bypass lines shall remain sealed closed during normal operation. | Meter bypass lines shall remain sealed closed during normal operation. | Flow_Meter_Project | Meter bypass lines shall remain locked and sealed closed during normal operation. | 0.6669 | 0.9718 | 0 | 0.9272 | 1 | None | {'Tool Unique Code': 38, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-038', 'Requirement Text': 'Meter bypass lines shall remain sealed closed during normal operation.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 19, '_indexed_description': 'Meter bypass lines shall remain sealed closed during normal operation.', '_containment_keys': ['meter bypass lines shall remain sealed closed during normal operation.']}
Flow_Meter_Company_Standard.xlsx | 29 | Custody transfer meters shall be verified every 6 months. | Custody transfer meters shall be verified every 6 months. | Flow_Meter_Project | Custody transfer meters shall be verified every 3 months. | 0.689 | 0.9857 | 0 | 0.9825 | 1 | None | {'Tool Unique Code': 48, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-048', 'Requirement Text': 'Custody transfer meters shall be verified every 6 months.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 29, '_indexed_description': 'Custody transfer meters shall be verified every 6 months.', '_containment_keys': ['custody transfer meters shall be verified every 6 months.']}
Flow_Meter_Company_Standard.xlsx | 8 | All metering parameter changes shall be recorded in an audit log. | All metering parameter changes shall be recorded in an audit log. | Flow_Meter_Project | All metering parameter changes shall be recorded in a secure audit log with timestamps. | 0.623 | 0.9258 | 0 | 0.8421 | 1 | None | {'Tool Unique Code': 27, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FM-027', 'Requirement Text': 'All metering parameter changes shall be recorded in an audit log.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 8, '_indexed_description': 'All metering parameter changes shall be recorded in an audit log.', '_containment_keys': ['all metering parameter changes shall be recorded in an audit log.']}
Flow_Meter_Company_Standard.xlsx | 17 | Isolation valves shall be installed upstream and downstream of each meter. | Isolation valves shall be installed upstream and downstream of each meter. | Flow_Meter_Project | Full-port isolation valves shall be installed upstream and downstream of each meter. | 0.957 | 0.94 | 1 | 0.9367 | 1 | None | {'Tool Unique Code': 36, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-036', 'Requirement Text': 'Isolation valves shall be installed upstream and downstream of each meter.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 17, '_indexed_description': 'Isolation valves shall be installed upstream and downstream of each meter.', '_containment_keys': ['isolation valves shall be installed upstream and downstream of each meter.']}
Flow_Meter_Company_Standard.xlsx | 24 | Temperature sensing elements shall be RTDs with accuracy of ±0.2°C. | Temperature sensing elements shall be RTDs with accuracy of ±0.2°C. | Flow_Meter_Project | Temperature sensing elements shall be dual RTDs with accuracy of ±0.1°C. | 0.665 | 0.9507 | 0 | 0.9489 | 1 | None | {'Tool Unique Code': 43, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-043', 'Requirement Text': 'Temperature sensing elements shall be RTDs with accuracy of ±0.2°C.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 24, '_indexed_description': 'Temperature sensing elements shall be RTDs with accuracy of ±0.2°C.', '_containment_keys': ['temperature sensing elements shall be rtds with accuracy of 0.2 c.']}
Flow_Meter_Company_Standard.xlsx | 4 | The metering system shall operate over a flow range of 20% to 100% of design flow. | The metering system shall operate over a flow range of 20% to 100% of design flow. | Flow_Meter_Project | The metering system shall operate over a flow range of 10% to 100% of design flow. | 0.692 | 0.9893 | 0 | 0.9875 | 1 | None | {'Tool Unique Code': 23, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-023', 'Requirement Text': 'The metering system shall operate over a flow range of 20% to 100% of design flow.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 4, '_indexed_description': 'The metering system shall operate over a flow range of 20% to 100% of design flow.', '_containment_keys': ['the metering system shall operate over a flow range of 20 to 100 of design flow.']}
Flow_Meter_Company_Standard.xlsx | 22 | Blowdown connections shall route fluids to a closed recovery system. | Blowdown connections shall route fluids to a closed recovery system. | Flow_Meter_Project | Blowdown connections shall route hydrocarbons to a vapor recovery system. | 0.5388 | 0.7194 | 0 | 0.8369 | 0.5 | None | {'Tool Unique Code': 41, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Environmental', 'Requirement ID': 'FM-041', 'Requirement Text': 'Blowdown connections shall route fluids to a closed recovery system.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 22, '_indexed_description': 'Blowdown connections shall route fluids to a closed recovery system.', '_containment_keys': ['blowdown connections shall route fluids to a closed recovery system.']}
Flow_Meter_Company_Standard.xlsx | 12 | All meter station equipment shall be properly grounded and bonded. | All meter station equipment shall be properly grounded and bonded. | Flow_Meter_Project | All meter station equipment shall be grounded, bonded, and surge protected. | 0.6058 | 0.9209 | 0 | 0.7914 | 0.6667 | None | {'Tool Unique Code': 31, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-031', 'Requirement Text': 'All meter station equipment shall be properly grounded and bonded.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 12, '_indexed_description': 'All meter station equipment shall be properly grounded and bonded.', '_containment_keys': ['all meter station equipment shall be properly grounded and bonded.']}
Electrical_Design_Basis_Company_Standard.xlsx | 8 | All electrical equipment shall be grounded and bonded to the plant grounding grid. | All electrical equipment shall be grounded and bonded to the plant grounding grid. | Flow_Meter_Project | All meter station equipment shall be grounded, bonded, and surge protected. | 0.5082 | 0.7575 | 0 | 0.6839 | 0.5 | Borderline score ¦ Low anchor overlap | {'Tool Unique Code': 55, 'Requirement Document': 'Electrical Design Basis Specification', 'Special Codes': 'Safety', 'Requirement ID': 'EDB-055', 'Requirement Text': 'All electrical equipment shall be grounded and bonded to the plant grounding grid.', '_source_file': 'Electrical_Design_Basis_Company_Standard.xlsx', '_source_row': 8, '_indexed_description': 'All electrical equipment shall be grounded and bonded to the plant grounding grid.', '_containment_keys': ['all electrical equipment shall be grounded and bonded to the plant grounding grid.']}
Flow_Meter_Company_Standard.xlsx | 6 | All custody transfer meters, provers, and flow computers shall include locks or tamper seals. | All custody transfer meters, provers, and flow computers shall include locks or tamper seals. | Flow_Meter_Project | All custody transfer meters, provers, and flow computers shall include locks, tamper seals, or electronic access control. | 0.6453 | 0.9786 | 0 | 0.8462 | 1 | None | {'Tool Unique Code': 25, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-025', 'Requirement Text': 'All custody transfer meters, provers, and flow computers shall include locks or tamper seals.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 6, '_indexed_description': 'All custody transfer meters, provers, and flow computers shall include locks or tamper seals.', '_containment_keys': ['all custody transfer meters provers and flow computers shall include locks or tamper seals.']}
Flow_Meter_Company_Standard.xlsx | 25 | A dedicated flow computer shall perform custody transfer calculations. | A dedicated flow computer shall perform custody transfer calculations. | Flow_Meter_Project | A redundant flow computer pair shall perform custody transfer calculations. The flow computer configuration shall support role-based access, secure parameter downloads, and event transfer to the metering workstation. | 0.4594 | 0.8051 | 0 | 0.4577 | 1 | Borderline score | {'Tool Unique Code': 44, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FM-044', 'Requirement Text': 'A dedicated flow computer shall perform custody transfer calculations.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 25, '_indexed_description': 'A dedicated flow computer shall perform custody transfer calculations.', '_containment_keys': ['a dedicated flow computer shall perform custody transfer calculations.']}
Flow_Meter_Company_Standard.xlsx | 15 | A minimum downstream straight pipe length of 5 diameters shall be provided. | A minimum downstream straight pipe length of 5 diameters shall be provided. | Flow_Meter_Project | A minimum downstream straight pipe length of 10 diameters shall be provided. | 0.6652 | 0.928 | 0 | 0.9801 | 1 | None | {'Tool Unique Code': 34, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-034', 'Requirement Text': 'A minimum downstream straight pipe length of 5 diameters shall be provided.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 15, '_indexed_description': 'A minimum downstream straight pipe length of 5 diameters shall be provided.', '_containment_keys': ['a minimum downstream straight pipe length of 5 diameters shall be provided.']}
Flow_Meter_Company_Standard.xlsx | 21 | Fill connections shall permit safe priming of meter runs. | Fill connections shall permit safe priming of meter runs. | Flow_Meter_Project | Fill connections shall permit safe meter run priming and flushing. | 0.6018 | 0.9314 | 0 | 0.7642 | 0.8 | None | {'Tool Unique Code': 40, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Environmental', 'Requirement ID': 'FM-040', 'Requirement Text': 'Fill connections shall permit safe priming of meter runs.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 21, '_indexed_description': 'Fill connections shall permit safe priming of meter runs.', '_containment_keys': ['fill connections shall permit safe priming of meter runs.']}
Flow_Meter_Company_Standard.xlsx | 9 | Calibration settings shall be password protected. | Calibration settings shall be password protected. | Flow_Meter_Project | Calibration settings shall be password protected and limited to administrator accounts. | 0.5941 | 0.9448 | 0 | 0.7206 | 1 | None | {'Tool Unique Code': 28, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FM-028', 'Requirement Text': 'Calibration settings shall be password protected.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 9, '_indexed_description': 'Calibration settings shall be password protected.', '_containment_keys': ['calibration settings shall be password protected.']}
Flow_Meter_Company_Standard.xlsx | 27 | Metering data shall be archived in the facility historian. | Metering data shall be archived in the facility historian. | Flow_Meter_Project | Metering data shall be archived in the PROJECT historian and backup server. | 0.5826 | 0.8701 | 0 | 0.782 | 0.6667 | None | {'Tool Unique Code': 46, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-046', 'Requirement Text': 'Metering data shall be archived in the facility historian.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 27, '_indexed_description': 'Metering data shall be archived in the facility historian.', '_containment_keys': ['metering data shall be archived in the facility historian.']}
Flow_Meter_Company_Standard.xlsx | 18 | Double block and bleed isolation shall be provided for prover connections. | Double block and bleed isolation shall be provided for prover connections. | Flow_Meter_Project | Double block and bleed isolation shall be provided for prover and calibration connections. | 0.6456 | 0.9373 | 0 | 0.9024 | 1 | None | {'Tool Unique Code': 37, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-037', 'Requirement Text': 'Double block and bleed isolation shall be provided for prover connections.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 18, '_indexed_description': 'Double block and bleed isolation shall be provided for prover connections.', '_containment_keys': ['double block and bleed isolation shall be provided for prover connections.']}
Flow_Meter_Company_Standard.xlsx | 11 | Intrinsic safety barriers shall be provided for field instrumentation in classified areas. | Intrinsic safety barriers shall be provided for field instrumentation in classified areas. | Flow_Meter_Project | Redundant intrinsic safety barriers shall be provided for field instrumentation in classified areas. | 0.9616 | 0.9436 | 1 | 0.9474 | 1 | None | {'Tool Unique Code': 30, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FM-030', 'Requirement Text': 'Intrinsic safety barriers shall be provided for field instrumentation in classified areas.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 11, '_indexed_description': 'Intrinsic safety barriers shall be provided for field instrumentation in classified areas.', '_containment_keys': ['intrinsic safety barriers shall be provided for field instrumentation in classified areas.']}
Flow_Meter_Company_Standard.xlsx | 26 | Critical measurement signals shall use redundant signal paths. | Critical measurement signals shall use redundant signal paths. | Flow_Meter_Project | Critical measurement signals shall use dual redundant signal paths. | 0.6808 | 0.9811 | 0 | 0.9612 | 1 | None | {'Tool Unique Code': 45, 'Requirement Document': 'Liquid Custody Transfer Specification', 'Special Codes': nan, 'Requirement ID': 'FM-045', 'Requirement Text': 'Critical measurement signals shall use redundant signal paths.', '_source_file': 'Flow_Meter_Company_Standard.xlsx', '_source_row': 26, '_indexed_description': 'Critical measurement signals shall use redundant signal paths.', '_containment_keys': ['critical measurement signals shall use redundant signal paths.']}

## Run Summary
Metric | Value
Comparison File | Flow_Meter_Project
Reference Dataset Name | Reference Dataset
Comparison Dataset Name | Comparison Dataset
Reference Compare Column | Requirement Text
Comparison Compare Column | Requirement Text
Description Confidence Score | 196
Total Comparison Rows | 28
Matched Comparison Rows | 26
Unmatched Comparison Rows | 2
Output Rows | 58
Processing Mode | all_gp_rows
Semantic Threshold | 0.55
Final Score Threshold | 0.44

## Platform Info
Item | Value
Platform | darwin
Excel COM Redline Available | No
Mac Rich Text Redline Available | Yes
Note | Windows uses Excel COM redline. Mac/non-Windows uses XlsxWriter rich text when available.