## Results
Tool Unique Code | Requirement Document | Special Codes | Requirement ID | Requirement Text | Comparison Dataset - Requirement ID | Special Code | Comparison Dataset - Requirement Text | Score | Match Rank | Match Diagnostics
1 | Access Control Specification | Cyber Security | ACS-001 | All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches. | 7.1.4 | nan | All ACS field panels, intelligent door controllers, IP-based card readers, and biometric readers shall connect to the PROJECT security network using managed Layer 3 Ethernet switches. | 0.616 | 1 | final=0.616; semantic=0.891; containment=0.000; fuzz=0.866; predicate_similarity=0.875; warnings=None; anchors=based,card,connect,controllers,door,ethernet,field,intelligent,managed,network,panels,readers,security,switches,using; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none
2 | Access Control Specification | Cyber Security | ACS-002 | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | 7.3.4 | Cyber Security | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | 1.0 | 1 | final=1.000; semantic=1.000; containment=1.000; fuzz=1.000; predicate_similarity=1.000; warnings=None; anchors=business,control,dedicated,networks,process,reside,separated,vlan; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none
3 | Access Control Specification | nan | ACS-003 | Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply. | 7.1.2 | nan | The access control panel power system shall include the following: each ACS control panel shall be powered from a dedicated 48 VDC regulated power supply; power supplies shall be mounted in lockable enclosures; and each power supply output shall be protected against overcurrent. | 0.441 | 2 | final=0.441; semantic=0.748; containment=0.000; fuzz=0.474; predicate_similarity=1.000; warnings=Borderline score; anchors=control,dedicated,each,panel,power,powered,regulated,supply; reference_object=control,each,panel; comparison_object=access,control,panel,power; reference_scope=none; comparison_scope=none
4 | Access Control Specification | nan | ACS-004 | ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS. | 7.3.2 | nan | ACS equipment shall maintain full operational capability for 8 hours following loss of primary power using UPS and battery backup. | 0.671 | 1 | final=0.671; semantic=0.977; containment=0.000; fuzz=0.934; predicate_similarity=1.000; warnings=None; anchors=backup,battery,capability,following,full,hours,loss,maintain,operational,power,primary,using; reference_object=none; comparison_object=none; reference_scope=hours following loss primary power using battery backup ups; comparison_scope=hours following loss primary power using ups battery backup
5 | Access Control Specification | nan | ACS-005 | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits. | 7.4.4 ----- 7.2.3 | nan ----- nan | All ACS control enclosures, reader junction boxes, field panels, and power supply cabinets shall include supervised tamper circuits. ----- The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.654 ----- 0.473 | 1 ----- 2 | final=0.654; semantic=0.980; containment=0.000; fuzz=0.873; predicate_similarity=1.000; warnings=None; anchors=boxes,circuits,control,enclosures,field,junction,panels,reader,supervised,tamper; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none ----- final=0.473; semantic=0.815; containment=0.000; fuzz=0.490; predicate_similarity=1.000; warnings=Borderline score; anchors=boxes,circuits,control,enclosures,field,junction,panels,reader,supervised,tamper; reference_object=none; comparison_object=enclosure,monitoring; reference_scope=none; comparison_scope=none
6 | Access Control Specification | nan | ACS-006 | Opening of a protected ACS enclosure shall generate an alarm at the central security workstation. | 7.2.3 | nan | The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.452 | 3 | final=0.452; semantic=0.795; containment=0.000; fuzz=0.447; predicate_similarity=0.600; warnings=Borderline score; anchors=central,enclosure,generate,opening,protected,security; reference_object=enclosure,opening,protected; comparison_object=enclosure,monitoring; reference_scope=none; comparison_scope=none
7 | Access Control Specification | nan | ACS-007 | Duress buttons shall be installed at control room entrances and security desks. | 7.4.1 | Safety | Duress buttons shall be installed at control room entrances, security desks, and gatehouses. | 0.659 | 1 | final=0.659; semantic=0.982; containment=0.000; fuzz=0.888; predicate_similarity=1.000; warnings=None; anchors=buttons,control,desks,duress,entrances,installed,room,security; reference_object=buttons,duress; comparison_object=buttons,duress; reference_scope=none; comparison_scope=none
8 | Access Control Specification | nan | ACS-008 | Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP). | 7.5.2 | nan | Copper ACS communication cabling shall be Category 6A shielded twisted pair (STP). | 0.695 | 1 | final=0.695; semantic=0.993; containment=0.000; fuzz=0.994; predicate_similarity=1.000; warnings=None; anchors=cabling,category,communication,copper,pair,shielded,twisted; reference_object=cabling,communication,copper; comparison_object=cabling,communication,copper; reference_scope=none; comparison_scope=none
9 | Access Control Specification | nan | ACS-009 | Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling. | 7.2.4 | nan | Inter-building ACS communication links exceeding 90 m shall use multimode fiber optic cabling. | 0.66 | 1 | final=0.660; semantic=0.955; containment=0.000; fuzz=0.927; predicate_similarity=1.000; warnings=None; anchors=building,cabling,communication,exceeding,fiber,inter,links,optic; reference_object=building,communication,exceeding,inter,links; comparison_object=building,communication,exceeding,inter,links; reference_scope=none; comparison_scope=none
10 | Access Control Specification | nan | ACS-010 | ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements. | 7.4.3 | nan | ACS equipment grounding shall comply with BICSI TDMM telecommunications grounding and bonding requirements. | 0.571 | 1 | final=0.571; semantic=0.730; containment=0.000; fuzz=0.929; predicate_similarity=1.000; warnings=None; anchors=bonding,comply,telecommunications; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none
11 | Access Control Specification | nan | ACS-011 | Each access-controlled door shall include a door position switch for monitoring door open and closed status.
12 | Access Control Specification | nan | ACS-012 | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | 7.3.3 | nan | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | 1.0 | 1 | final=1.000; semantic=1.000; containment=1.000; fuzz=1.000; predicate_similarity=1.000; warnings=None; anchors=access,controlled,controller,door,each,exit,integrated,request; reference_object=access,controlled,door,each; comparison_object=access,controlled,door,each; reference_scope=none; comparison_scope=none
13 | Access Control Specification | nan | ACS-013 | Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification. | 7.5.3 | Safety | Electric locking hardware shall fail safe or fail secure as defined in the PROJECT Facility Design Specification and fire alarm cause-and-effect matrix. | 0.612 | 1 | final=0.612; semantic=0.917; containment=0.000; fuzz=0.817; predicate_similarity=1.000; warnings=None; anchors=defined,electric,facility,fail,hardware,locking,safe,secure,specification; reference_object=electric,hardware,locking; comparison_object=electric,hardware,locking; reference_scope=none; comparison_scope=none
14 | Access Control Specification | nan | ACS-014 | Card readers installed in hazardous areas shall be certified for the applicable area classification.
15 | Access Control Specification | Cyber Security | ACS-015 | ACS controllers shall retain local decision-making capability during network communication loss.
16 | Access Control Specification | Cyber Security | ACS-016 | ACS event logs shall be buffered locally for a minimum of 10000 events during network outage. | 7.3.1 | Cyber Security | ACS event logs shall be buffered locally for a minimum of 20000 events during network outage. | 0.695 | 1 | final=0.695; semantic=0.997; containment=0.000; fuzz=0.989; predicate_similarity=0.875; warnings=None; anchors=buffered,during,event,events,locally,logs,minimum,network,outage; reference_object=event,logs; comparison_object=event,logs; reference_scope=minimum 10000 events during network outage; comparison_scope=minimum 20000 events during network outage
17 | Access Control Specification | nan | ACS-017 | All ACS field wiring shall be clearly labeled at both ends using permanent machine-printed labels.
18 | Access Control Specification | nan | ACS-018 | ACS control panels shall include surge protection for power and communication interfaces. | 7.1.3 | nan | ACS control panels shall include surge protection for all power, communication, and I/O interfaces. | 0.661 | 1 | final=0.661; semantic=0.967; containment=0.000; fuzz=0.914; predicate_similarity=1.000; warnings=None; anchors=communication,control,interfaces,panels,power,protection,surge; reference_object=control,panels; comparison_object=control,panels; reference_scope=power communication interfaces; comparison_scope=all power
19 | Access Control Specification | nan | ACS-019 | Door lock power circuits shall be individually fused or electronically protected against overcurrent.
20 | Access Control Specification | Cyber Security | ACS-020 | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | 7.2.2 | Cyber Security | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | 1.0 | 1 | final=1.000; semantic=1.000; containment=1.000; fuzz=1.000; predicate_similarity=1.000; warnings=None; anchors=facility,operator,redundant,servers,sources,synchronize,time,using,workstations; reference_object=operator,servers,workstations; comparison_object=operator,servers,workstations; reference_scope=none; comparison_scope=none
97 | Access Control Specification | Cyber Security | ACS-021 | The ACS shall support anti-passback logic to prevent credential sharing and unauthorized re-entry.
98 | Access Control Specification | Cyber Security | ACS-022 | The ACS credential database shall be automatically backed up daily to a secure redundant storage location.
99 | Access Control Specification | Safety | ACS-023 | The ACS shall generate a forced-open alarm when a controlled door remains open longer than the configured timeout period.
100 | Access Control Specification | Cyber Security | ACS-024 | Central ACS servers shall be deployed in a redundant primary-secondary architecture with automatic failover.
101 | Access Control Specification | nan | ACS-025 | The ACS shall support integration with the video management system for alarm-triggered video association.
77 | Facility Security Systems Specification | Cyber Security | FSS-101 | Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources. | 7.2.2 | Cyber Security | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | 0.639 | 2 | final=0.639; semantic=0.916; containment=0.000; fuzz=0.910; predicate_similarity=1.000; warnings=None; anchors=facility,operator,redundant,servers,sources,synchronize,time,using,workstations; reference_object=operator,security,servers,workstations; comparison_object=operator,servers,workstations; reference_scope=none; comparison_scope=none
78 | Facility Security Systems Specification | nan | FSS-102 | Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches. | 7.1.4 | nan | All ACS field panels, intelligent door controllers, IP-based card readers, and biometric readers shall connect to the PROJECT security network using managed Layer 3 Ethernet switches. | 0.6 | 2 | final=0.600; semantic=0.871; containment=0.000; fuzz=0.840; predicate_similarity=1.000; warnings=None; anchors=biometric,card,connect,controllers,door,ethernet,field,managed,network,panels,readers,security,switches,using; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none
79 | Facility Security Systems Specification | Cyber Security | FSS-103 | Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks. | 7.3.4 | Cyber Security | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | 0.542 | 2 | final=0.542; semantic=0.708; containment=0.000; fuzz=0.862; predicate_similarity=0.875; warnings=None; anchors=business,control,dedicated,networks,process,separated,vlan; reference_object=security; comparison_object=none; reference_scope=none; comparison_scope=none
80 | Facility Security Systems Specification | nan | FSS-104 | Security control panels shall include surge protection on power, communications, and field I/O circuits.
81 | Facility Security Systems Specification | Safety | FSS-105 | Card readers and field security devices installed in hazardous classified areas shall be certified for the applicable area classification.
82 | Facility Security Systems Specification | nan | FSS-106 | Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs. | 7.1.2 | nan | The access control panel power system shall include the following: each ACS control panel shall be powered from a dedicated 48 VDC regulated power supply; power supplies shall be mounted in lockable enclosures; and each power supply output shall be protected against overcurrent. | 0.48 | 1 | final=0.480; semantic=0.765; containment=0.000; fuzz=0.582; predicate_similarity=0.875; warnings=Borderline score; anchors=control,enclosures,lockable,mounted,panel,power,protected,regulated,supplies; reference_object=control,panel,power,security; comparison_object=access,control,panel,power; reference_scope=none; comparison_scope=none
83 | Facility Security Systems Specification | nan | FSS-107 | Access-controlled doors shall include door position monitoring to indicate secure, open, and forced-open conditions.
84 | Facility Security Systems Specification | nan | FSS-108 | Access-controlled doors shall include request-to-exit devices connected to the door controller. | 7.3.3 | nan | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | 0.618 | 2 | final=0.618; semantic=0.906; containment=0.000; fuzz=0.853; predicate_similarity=0.750; warnings=None; anchors=access,controlled,controller,door,exit,request; reference_object=access,controlled,doors; comparison_object=access,controlled,door,each; reference_scope=none; comparison_scope=none
85 | Facility Security Systems Specification | nan | FSS-109 | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits. | 7.4.4 ----- 7.2.3 | nan ----- nan | All ACS control enclosures, reader junction boxes, field panels, and power supply cabinets shall include supervised tamper circuits. ----- The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.609 ----- 0.486 | 2 ----- 1 | final=0.609; semantic=0.904; containment=0.000; fuzz=0.823; predicate_similarity=1.000; warnings=None; anchors=boxes,cabinets,circuits,control,enclosures,junction,panels,power,reader,supervised,supply,tamper; reference_object=none; comparison_object=none; reference_scope=none; comparison_scope=none ----- final=0.486; semantic=0.801; containment=0.000; fuzz=0.554; predicate_similarity=1.000; warnings=Borderline score; anchors=boxes,cabinets,circuits,control,enclosures,junction,panels,power,reader,security,supervised,supply,tamper; reference_object=none; comparison_object=enclosure,monitoring; reference_scope=none; comparison_scope=none
86 | Facility Security Systems Specification | nan | FSS-110 | Opening of a protected security enclosure shall generate an alarm at the central security workstation.
87 | Facility Security Systems Specification | Safety | FSS-111 | Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations. | 7.4.1 | Safety | Duress buttons shall be installed at control room entrances, security desks, and gatehouses. | 0.607 | 2 | final=0.607; semantic=0.967; containment=0.000; fuzz=0.734; predicate_similarity=0.714; warnings=None; anchors=buttons,control,desks,duress,entrances,room,security; reference_object=buttons,duress; comparison_object=buttons,duress; reference_scope=none; comparison_scope=none
88 | Facility Security Systems Specification | nan | FSS-112 | Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling. | 7.2.4 | nan | Inter-building ACS communication links exceeding 90 m shall use multimode fiber optic cabling. | 0.464 | 2 | final=0.464; semantic=0.716; containment=0.000; fuzz=0.591; predicate_similarity=1.000; warnings=Borderline score; anchors=cabling,communication,fiber,links,optic; reference_object=between,buildings,communication,copper,distance,ethernet,exceed,limitations,links,security; comparison_object=building,communication,exceeding,inter,links; reference_scope=none; comparison_scope=none
89 | Facility Security Systems Specification | nan | FSS-113 | Facility security system cabling shall be shielded twisted pair or fiber optic cable suitable for the installed environment.
90 | Facility Security Systems Specification | nan | FSS-114 | Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard. | 7.4.3 | nan | ACS equipment grounding shall comply with BICSI TDMM telecommunications grounding and bonding requirements. | 0.5 | 2 | final=0.500; semantic=0.712; containment=0.000; fuzz=0.719; predicate_similarity=0.500; warnings=Borderline score; anchors=bonding,comply,telecommunications; reference_object=bonding,security; comparison_object=none; reference_scope=none; comparison_scope=none
91 | Facility Security Systems Specification | Cyber Security | FSS-115 | Security system event logs shall be retained locally during network outages and forwarded to the security workstation when communications are restored.
92 | Facility Security Systems Specification | nan | FSS-116 | Security controllers shall support local access decisions during loss of communication with the central server.
93 | Facility Security Systems Specification | Safety | FSS-117 | Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis. | 7.5.3 | Safety | Electric locking hardware shall fail safe or fail secure as defined in the PROJECT Facility Design Specification and fire alarm cause-and-effect matrix. | 0.509 | 2 | final=0.509; semantic=0.857; containment=0.000; fuzz=0.556; predicate_similarity=0.818; warnings=Borderline score; anchors=alarm,cause,effect,electric,facility,fail,fire,hardware,locking,matrix,safe,secure; reference_object=door,electric,hardware,locking; comparison_object=electric,hardware,locking; reference_scope=none; comparison_scope=none
94 | Facility Security Systems Specification | nan | FSS-118 | Security field wiring shall be permanently labeled at both ends, and spare conductors shall be identified and isolated.
95 | Facility Security Systems Specification | nan | FSS-119 | Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions. | 7.5.1 | nan | Door lock power circuits shall be individually fused and continuously monitored for overcurrent conditions. | 0.583 | 1 | final=0.583; semantic=0.886; containment=0.000; fuzz=0.763; predicate_similarity=0.667; warnings=None; anchors=circuits,conditions,door,individually,lock,monitored,overcurrent,power; reference_object=circuits,door,lock,power; comparison_object=circuits,door,lock,power; reference_scope=abnormal power conditions; comparison_scope=overcurrent conditions
96 | Facility Security Systems Specification | Cyber Security | FSS-120 | The security system shall record access control events, door alarms, enclosure tamper events, and operator actions in an auditable event log.
[5 empty] | 7.1.1 | nan | Each access-controlled door shall include redundant door position switches for monitoring secure and open status.
[5 empty] | 7.2.1 | Safety | Card readers installed in hazardous areas shall be certified for Zone 1 hazardous area classification per IEC 60079.
[5 empty] | 7.4.2 | nan | ACS controllers shall retain autonomous local decision-making capability during network communication loss for a minimum of 24 hours.
[5 empty] | 7.5.4 | nan | ACS field installation requirements shall include the following: all ACS field wiring shall be labeled at both ends using permanent engraved labels; cable shields shall be terminated in accordance with the grounding standard; and spare conductors shall be identified and isolated.

## Diagnostics
Reference Source File | Reference Source Row | Reference Compare Text | Reference Indexed Description | Comparison Source File | Comparison Compare Text | Final Score | Semantic Score | Containment Score | Fuzzy Score | Predicate Similarity | Potential Issue | Reference Full Row
Facility_Security_Systems_Company_Standard.xlsx | 7 | Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs. | Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs. | ACS_Requirements_Project | The access control panel power system shall include the following: each ACS control panel shall be powered from a dedicated 48 VDC regulated power supply; power supplies shall be mounted in lockable enclosures; and each power supply output shall be protected against overcurrent. | 0.4804 | 0.7645 | 0 | 0.5819 | 0.875 | Borderline score | {'Tool Unique Code': 82, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-106', 'Requirement Text': 'Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 7, '_indexed_description': 'Security control panel power systems shall include regulated DC power supplies mounted in lockable enclosures with protected outputs.', '_containment_keys': ['security control panel power systems shall include regulated dc power supplies mounted in lockable enclosures with protected outputs.']}
Access Control Systens - Company Standard.xlsx | 4 | Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply. | Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply. | ACS_Requirements_Project | The access control panel power system shall include the following: each ACS control panel shall be powered from a dedicated 48 VDC regulated power supply; power supplies shall be mounted in lockable enclosures; and each power supply output shall be protected against overcurrent. | 0.4412 | 0.7476 | 0 | 0.4738 | 1 | Borderline score | {'Tool Unique Code': 3, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-003', 'Requirement Text': 'Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 4, '_indexed_description': 'Each ACS control panel shall be powered from a dedicated 24 VDC regulated power supply.', '_containment_keys': ['each acs control panel shall be powered from a dedicated 24 vdc regulated power supply.']}
Access Control Systens - Company Standard.xlsx | 19 | ACS control panels shall include surge protection for power and communication interfaces. | ACS control panels shall include surge protection for power and communication interfaces. | ACS_Requirements_Project | ACS control panels shall include surge protection for all power, communication, and I/O interfaces. | 0.6611 | 0.9674 | 0 | 0.914 | 1 | None | {'Tool Unique Code': 18, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-018', 'Requirement Text': 'ACS control panels shall include surge protection for power and communication interfaces.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 19, '_indexed_description': 'ACS control panels shall include surge protection for power and communication interfaces.', '_containment_keys': ['acs control panels shall include surge protection for power and communication interfaces.']}
Access Control Systens - Company Standard.xlsx | 2 | All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches. | All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches. | ACS_Requirements_Project | All ACS field panels, intelligent door controllers, IP-based card readers, and biometric readers shall connect to the PROJECT security network using managed Layer 3 Ethernet switches. | 0.6159 | 0.8906 | 0 | 0.8657 | 0.875 | None | {'Tool Unique Code': 1, 'Requirement Document': 'Access Control Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'ACS-001', 'Requirement Text': 'All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 2, '_indexed_description': 'All ACS field panels, intelligent door controllers, and IP-based card readers shall connect to the facility security network using managed Ethernet switches.', '_containment_keys': ['all acs field panels intelligent door controllers and ip-based card readers shall connect to the facility security network using managed ethernet switches.']}
Facility_Security_Systems_Company_Standard.xlsx | 3 | Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches. | Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches. | ACS_Requirements_Project | All ACS field panels, intelligent door controllers, IP-based card readers, and biometric readers shall connect to the PROJECT security network using managed Layer 3 Ethernet switches. | 0.6004 | 0.8712 | 0 | 0.8397 | 1 | None | {'Tool Unique Code': 78, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-102', 'Requirement Text': 'Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 3, '_indexed_description': 'Facility security system field panels, door controllers, IP card readers, and biometric readers shall connect to the security network using managed Ethernet switches.', '_containment_keys': ['facility security system field panels door controllers ip card readers and biometric readers shall connect to the security network using managed ethernet switches.']}
Access Control Systens - Company Standard.xlsx | 21 | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | ACS_Requirements_Project | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | 1 | 1 | 1 | 1 | 1 | None | {'Tool Unique Code': 20, 'Requirement Document': 'Access Control Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'ACS-020', 'Requirement Text': 'ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 21, '_indexed_description': 'ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources.', '_containment_keys': ['acs servers and operator workstations shall synchronize system time using redundant facility-approved ntp sources.']}
Facility_Security_Systems_Company_Standard.xlsx | 2 | Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources. | Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources. | ACS_Requirements_Project | ACS servers and operator workstations shall synchronize system time using redundant facility-approved NTP sources. | 0.6392 | 0.9155 | 0 | 0.9099 | 1 | None | {'Tool Unique Code': 77, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FSS-101', 'Requirement Text': 'Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 2, '_indexed_description': 'Security system servers and operator workstations shall synchronize time using redundant facility-approved NTP sources.', '_containment_keys': ['security system servers and operator workstations shall synchronize time using redundant facility-approved ntp sources.']}
Facility_Security_Systems_Company_Standard.xlsx | 10 | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits. | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits. | ACS_Requirements_Project | The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.4864 | 0.8008 | 0 | 0.5535 | 1 | Borderline score | {'Tool Unique Code': 85, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-109', 'Requirement Text': 'Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 10, '_indexed_description': 'Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits.', '_containment_keys': ['security enclosures access control panels reader junction boxes and power supply cabinets shall include supervised tamper circuits.']}
Access Control Systens - Company Standard.xlsx | 6 | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits. | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits. | ACS_Requirements_Project | The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.4731 | 0.815 | 0 | 0.4903 | 1 | Borderline score | {'Tool Unique Code': 5, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-005', 'Requirement Text': 'All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 6, '_indexed_description': 'All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits.', '_containment_keys': ['all acs control enclosures reader junction boxes and field panels shall include supervised tamper circuits.']}
Access Control Systens - Company Standard.xlsx | 7 | Opening of a protected ACS enclosure shall generate an alarm at the central security workstation. | Opening of a protected ACS enclosure shall generate an alarm at the central security workstation. | ACS_Requirements_Project | The ACS enclosure monitoring design shall include supervised tamper circuits on control enclosures, reader junction boxes, field panels, and power supply cabinets. Opening of a protected ACS enclosure shall generate both local and central security alarms. | 0.4521 | 0.7949 | 0 | 0.447 | 0.6 | Borderline score | {'Tool Unique Code': 6, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-006', 'Requirement Text': 'Opening of a protected ACS enclosure shall generate an alarm at the central security workstation.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 7, '_indexed_description': 'Opening of a protected ACS enclosure shall generate an alarm at the central security workstation.', '_containment_keys': ['opening of a protected acs enclosure shall generate an alarm at the central security workstation.']}
Access Control Systens - Company Standard.xlsx | 10 | Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling. | Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling. | ACS_Requirements_Project | Inter-building ACS communication links exceeding 90 m shall use multimode fiber optic cabling. | 0.6602 | 0.9551 | 0 | 0.9274 | 1 | None | {'Tool Unique Code': 9, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-009', 'Requirement Text': 'Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 10, '_indexed_description': 'Inter-building ACS communication links exceeding 100 m shall use fiber optic cabling.', '_containment_keys': ['inter-building acs communication links exceeding 100 m shall use fiber optic cabling.']}
Facility_Security_Systems_Company_Standard.xlsx | 13 | Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling. | Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling. | ACS_Requirements_Project | Inter-building ACS communication links exceeding 90 m shall use multimode fiber optic cabling. | 0.4638 | 0.7162 | 0 | 0.5909 | 1 | Borderline score | {'Tool Unique Code': 88, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-112', 'Requirement Text': 'Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 13, '_indexed_description': 'Security communication links between buildings that exceed copper Ethernet distance limitations shall use fiber optic cabling.', '_containment_keys': ['security communication links between buildings that exceed copper ethernet distance limitations shall use fiber optic cabling.']}
Access Control Systens - Company Standard.xlsx | 17 | ACS event logs shall be buffered locally for a minimum of 10000 events during network outage. | ACS event logs shall be buffered locally for a minimum of 10000 events during network outage. | ACS_Requirements_Project | ACS event logs shall be buffered locally for a minimum of 20000 events during network outage. | 0.6954 | 0.9966 | 0 | 0.9892 | 0.875 | None | {'Tool Unique Code': 16, 'Requirement Document': 'Access Control Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'ACS-016', 'Requirement Text': 'ACS event logs shall be buffered locally for a minimum of 10000 events during network outage.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 17, '_indexed_description': 'ACS event logs shall be buffered locally for a minimum of 10000 events during network outage.', '_containment_keys': ['acs event logs shall be buffered locally for a minimum of 10000 events during network outage.']}
Access Control Systens - Company Standard.xlsx | 5 | ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS. | ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS. | ACS_Requirements_Project | ACS equipment shall maintain full operational capability for 8 hours following loss of primary power using UPS and battery backup. | 0.671 | 0.9768 | 0 | 0.9344 | 1 | None | {'Tool Unique Code': 4, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-004', 'Requirement Text': 'ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 5, '_indexed_description': 'ACS equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or UPS.', '_containment_keys': ['acs equipment shall maintain full operational capability for 4 hours following loss of primary power using battery backup or ups.']}
Access Control Systens - Company Standard.xlsx | 13 | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | ACS_Requirements_Project | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | 1 | 1 | 1 | 1 | 1 | None | {'Tool Unique Code': 12, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-012', 'Requirement Text': 'Each access-controlled door shall include a request-to-exit device integrated with the ACS controller.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 13, '_indexed_description': 'Each access-controlled door shall include a request-to-exit device integrated with the ACS controller.', '_containment_keys': ['each access-controlled door shall include a request-to-exit device integrated with the acs controller.']}
Facility_Security_Systems_Company_Standard.xlsx | 9 | Access-controlled doors shall include request-to-exit devices connected to the door controller. | Access-controlled doors shall include request-to-exit devices connected to the door controller. | ACS_Requirements_Project | Each access-controlled door shall include a request-to-exit device integrated with the ACS controller. | 0.6181 | 0.9056 | 0 | 0.8528 | 0.75 | None | {'Tool Unique Code': 84, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-108', 'Requirement Text': 'Access-controlled doors shall include request-to-exit devices connected to the door controller.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 9, '_indexed_description': 'Access-controlled doors shall include request-to-exit devices connected to the door controller.', '_containment_keys': ['access-controlled doors shall include request-to-exit devices connected to the door controller.']}
Access Control Systens - Company Standard.xlsx | 3 | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | ACS_Requirements_Project | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | 1 | 1 | 1 | 1 | 1 | None | {'Tool Unique Code': 2, 'Requirement Document': 'Access Control Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'ACS-002', 'Requirement Text': 'ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 3, '_indexed_description': 'ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks.', '_containment_keys': ['acs devices shall reside on a dedicated vlan separated from business networks and process control networks.']}
Facility_Security_Systems_Company_Standard.xlsx | 4 | Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks. | Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks. | ACS_Requirements_Project | ACS devices shall reside on a dedicated VLAN separated from business networks and process control networks. | 0.5421 | 0.7085 | 0 | 0.8622 | 0.875 | None | {'Tool Unique Code': 79, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': 'Cyber Security', 'Requirement ID': 'FSS-103', 'Requirement Text': 'Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 4, '_indexed_description': 'Security devices shall be installed on a dedicated VLAN separated from business, wireless, and process control networks.', '_containment_keys': ['security devices shall be installed on a dedicated vlan separated from business wireless and process control networks.']}
Access Control Systens - Company Standard.xlsx | 8 | Duress buttons shall be installed at control room entrances and security desks. | Duress buttons shall be installed at control room entrances and security desks. | ACS_Requirements_Project | Duress buttons shall be installed at control room entrances, security desks, and gatehouses. | 0.6589 | 0.9816 | 0 | 0.8876 | 1 | None | {'Tool Unique Code': 7, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-007', 'Requirement Text': 'Duress buttons shall be installed at control room entrances and security desks.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 8, '_indexed_description': 'Duress buttons shall be installed at control room entrances and security desks.', '_containment_keys': ['duress buttons shall be installed at control room entrances and security desks.']}
Facility_Security_Systems_Company_Standard.xlsx | 12 | Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations. | Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations. | ACS_Requirements_Project | Duress buttons shall be installed at control room entrances, security desks, and gatehouses. | 0.6071 | 0.9671 | 0 | 0.734 | 0.7143 | None | {'Tool Unique Code': 87, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FSS-111', 'Requirement Text': 'Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 12, '_indexed_description': 'Duress buttons shall be provided at security desks, control room entrances, and gatehouse locations.', '_containment_keys': ['duress buttons shall be provided at security desks control room entrances and gatehouse locations.']}
Access Control Systens - Company Standard.xlsx | 11 | ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements. | ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements. | ACS_Requirements_Project | ACS equipment grounding shall comply with BICSI TDMM telecommunications grounding and bonding requirements. | 0.5707 | 0.73 | 0 | 0.9289 | 1 | None | {'Tool Unique Code': 10, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-010', 'Requirement Text': 'ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 11, '_indexed_description': 'ACS equipment grounding shall comply with TIA-607 telecommunications grounding and bonding requirements.', '_containment_keys': ['acs equipment grounding shall comply with tia-607 telecommunications grounding and bonding requirements.']}
Facility_Security_Systems_Company_Standard.xlsx | 15 | Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard. | Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard. | ACS_Requirements_Project | ACS equipment grounding shall comply with BICSI TDMM telecommunications grounding and bonding requirements. | 0.5003 | 0.7116 | 0 | 0.7189 | 0.5 | Borderline score | {'Tool Unique Code': 90, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-114', 'Requirement Text': 'Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 15, '_indexed_description': 'Security equipment grounding and bonding shall comply with the facility telecommunications grounding standard.', '_containment_keys': ['security equipment grounding and bonding shall comply with the facility telecommunications grounding standard.']}
Access Control Systens - Company Standard.xlsx | 6 | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits. | All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits. | ACS_Requirements_Project | All ACS control enclosures, reader junction boxes, field panels, and power supply cabinets shall include supervised tamper circuits. | 0.6537 | 0.9797 | 0 | 0.8729 | 1 | None | {'Tool Unique Code': 5, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-005', 'Requirement Text': 'All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 6, '_indexed_description': 'All ACS control enclosures, reader junction boxes, and field panels shall include supervised tamper circuits.', '_containment_keys': ['all acs control enclosures reader junction boxes and field panels shall include supervised tamper circuits.']}
Facility_Security_Systems_Company_Standard.xlsx | 10 | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits. | Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits. | ACS_Requirements_Project | All ACS control enclosures, reader junction boxes, field panels, and power supply cabinets shall include supervised tamper circuits. | 0.6087 | 0.9045 | 0 | 0.8231 | 1 | None | {'Tool Unique Code': 85, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-109', 'Requirement Text': 'Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 10, '_indexed_description': 'Security enclosures, access control panels, reader junction boxes, and power supply cabinets shall include supervised tamper circuits.', '_containment_keys': ['security enclosures access control panels reader junction boxes and power supply cabinets shall include supervised tamper circuits.']}
Facility_Security_Systems_Company_Standard.xlsx | 20 | Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions. | Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions. | ACS_Requirements_Project | Door lock power circuits shall be individually fused and continuously monitored for overcurrent conditions. | 0.5833 | 0.8858 | 0 | 0.7632 | 0.6667 | None | {'Tool Unique Code': 95, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': nan, 'Requirement ID': 'FSS-119', 'Requirement Text': 'Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 20, '_indexed_description': 'Door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions.', '_containment_keys': ['door lock power circuits shall be individually protected against overcurrent and monitored for abnormal power conditions.']}
Access Control Systens - Company Standard.xlsx | 9 | Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP). | Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP). | ACS_Requirements_Project | Copper ACS communication cabling shall be Category 6A shielded twisted pair (STP). | 0.6954 | 0.993 | 0 | 0.9939 | 1 | None | {'Tool Unique Code': 8, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-008', 'Requirement Text': 'Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP).', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 9, '_indexed_description': 'Copper ACS communication cabling shall be Category 6 shielded twisted pair (STP).', '_containment_keys': ['copper acs communication cabling shall be category 6 shielded twisted pair (stp).']}
Access Control Systens - Company Standard.xlsx | 14 | Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification. | Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification. | ACS_Requirements_Project | Electric locking hardware shall fail safe or fail secure as defined in the PROJECT Facility Design Specification and fire alarm cause-and-effect matrix. | 0.612 | 0.9172 | 0 | 0.8171 | 1 | None | {'Tool Unique Code': 13, 'Requirement Document': 'Access Control Specification', 'Special Codes': nan, 'Requirement ID': 'ACS-013', 'Requirement Text': 'Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification.', '_source_file': 'Access Control Systens - Company Standard.xlsx', '_source_row': 14, '_indexed_description': 'Electric locking hardware shall fail safe or fail secure as defined in the Facility Design Specification.', '_containment_keys': ['electric locking hardware shall fail safe or fail secure as defined in the facility design specification.']}
Facility_Security_Systems_Company_Standard.xlsx | 18 | Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis. | Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis. | ACS_Requirements_Project | Electric locking hardware shall fail safe or fail secure as defined in the PROJECT Facility Design Specification and fire alarm cause-and-effect matrix. | 0.5094 | 0.8569 | 0 | 0.5556 | 0.8182 | Borderline score | {'Tool Unique Code': 93, 'Requirement Document': 'Facility Security Systems Specification', 'Special Codes': 'Safety', 'Requirement ID': 'FSS-117', 'Requirement Text': 'Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis.', '_source_file': 'Facility_Security_Systems_Company_Standard.xlsx', '_source_row': 18, '_indexed_description': 'Electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis.', '_containment_keys': ['electric door locking hardware shall be coordinated with the fire alarm cause-and-effect matrix and shall fail safe or fail secure as required by the facility design basis.']}

## Run Summary
Metric | Value
Comparison File | ACS_Requirements_Project
Reference Dataset Name | Reference Dataset
Comparison Dataset Name | Comparison Dataset
Reference Compare Column | Requirement Text
Comparison Compare Column | Requirement Text
Description Confidence Score | 140
Total Comparison Rows | 20
Matched Comparison Rows | 16
Unmatched Comparison Rows | 4
Output Rows | 49
Processing Mode | all_gp_rows
Semantic Threshold | 0.55
Final Score Threshold | 0.44

## Platform Info
Item | Value
Platform | darwin
Excel COM Redline Available | No
Mac Rich Text Redline Available | Yes
Note | Windows uses Excel COM redline. Mac/non-Windows uses XlsxWriter rich text when available.